## Summary
Workflow Document Tracker
Row Labels | Count of (Helper) Doc Status | Project Name: FS1018 DfE Wisbech Free School | Total number of documents: 588
A - Accepted | 229 | Date Generated: 24/04/2025
Pending | 359 | Summary Page
Grand Total | 588
Total number of documents: 588

## Tracker
Stage 4 Workflow Document Tracker |  |  |  |  | Click here to go to your outstanding workflows
Project Name: FS1018 DfE Wisbech Free School
Date Generated: 24/04/2025
Number | (All)
| Date In | Step Name | Step Outcome | Date of Comments | Comments
FS1018-ADT-ZZ-00-D-J-0001 BB93 Acoustic Criteria Ground Floor
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Why is there no acoustic performance for the library partition alongside the corridor. The library door should have a 30dB acoustic rating in line with BB93.
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-ADT-ZZ-00-D-J-0004 Acoustic Wall Types Ground Floor
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01
FS1018-ADT-ZZ-01-D-J-0002 BB93 Acoustic Criteria First Floor
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01
FS1018-ADT-ZZ-01-D-J-0005 Acoustic Wall Types First Floor
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01
FS1018-ADT-ZZ-02-D-J-0003 BB93 Acoustic Criteria Second Floor
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01
FS1018-ADT-ZZ-02-D-J-0006 Acoustic Wall Types Second Floor
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01
FS1018-ADT-ZZ-ZZ-T-J-0001 Acoustic Strategy
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Why is there no acoustic performance for the library partition alongside the corridor. The library door should have a 30dB acoustic rating in line with BB93.
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-ADT-ZZ-ZZ-T-Y-0002 Environmental Noise Impact Assessment
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 | No further comments
FS1018-AGL-ZZ-00-D-E-6110 Level 00 Containment Sheet 1
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-00-D-E-6111 Level 00 Containment Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-00-D-E-6112 Level 00 Containment Sheet 3
P01 | 2025-03-14 | DFE Review | C - Rejected | 2025-04-02 | Intake duct location not as shown in FS1018-AGL-ZZ-XX-D-E-9511
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-00-D-E-6114 Building Electrical Switchroom Details
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-00-D-E-6210 Level 00 Small Power And Data Sheet 1
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-00-D-E-6211 Level 00 Small Power And Data Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-00-D-E-6212 Level 00 Small Power And Data Sheet 3
P01 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-02 | Consider adding a general power outlet in the plantroom for maintenance and cleaning
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-00-D-E-6213 Level 00 MSER Sheet 1
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-00-D-E-6214 Level 00 MSER Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-00-D-E-6215 Level 00 MSER Sheet 3
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-00-D-E-6310 Level 00 Lighting Sheet 1
P01 | 2025-03-14 | DFE Review | C - Rejected | 2025-04-02 | General and Emergency Lighting not shown for maintenace stair between gridlines A and B. Consider emergency light outside exit at gridline 3A/A and dishwash room. Additional Exit signage shown in Fire Stratergy Report FS1018-OFR-XX-ZZ-G-K-0001 Appendix B. In locations shown yellow in image below and Ground floor gridlines 3A/A, 5/E, 5/K1, 5/M1, 6A/W, 4A/S, 5/R and 6/R
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-00-D-E-6311 Level 00 Lighting Sheet 2
P01 | 2025-03-14 | DFE Review | C - Rejected | 2025-04-02 | 1.Additional Exit signage shown in Fire Strategy Report FS1018-OFR-XX-ZZ-G-K-0001 Appendix B, in locations on Ground floor gridlines 3A/A, 5/E, 5/K1, 5/M1, 6A/W, 4A/S, 5/R and 6/R 2.Confirm if area of 01-1101 ICT Classroom 1 and 01-1102 ICT Classroom 2 is les than 60m (as emergency lighting required if over 60m)
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-00-D-E-6312 Level 00 Lighting Sheet 3
P01 | 2025-03-14 | DFE Review | C - Rejected | 2025-04-02 | Additional Exit signage shown in Fire Strategy Report FS1018-OFR-XX-ZZ-G-K-0001 Appendix B, in locations on Ground floor gridlines 3A/A, 5/E, 5/K1, 5/M1, 6A/W, 4A/S, 5/R and 6/R Emergency lighting for Rm 00-4015 OFF12 (as you have to go through this room to get to the inner room STN50)
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-00-D-E-6810 Level 00 Fire Alarm Sheet 1
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-00-D-E-6811 Level 00 Fire Alarm Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-00-D-E-6812 Level 00 Fire Alarm Sheet 3
P01 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-02 | Contractor to confirm that a fire detection devise is located within 1.5 m from the lift shaft opening On activation of the first silent alarm how is the staff member informed in order to investigate and has this been confirmed with the fire engineer. Interfaces 'GS' is not included in the acronyms
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-00-D-E-6820 Level 00 Fire Alarm Zoning Sheet 1
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-00-D-E-6821 Level 00 Fire Alarm Zoning Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-00-D-E-6822 Level 00 Fire Alarm Zoning Sheet 3
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-00-D-E-6840 Level 00 Security Sheet 1
P01 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-02 | Please confirm that the security, access control and CCTV are to be designed and commissioned by the specialist and the details on the drawing have been reviewed and agreed with the school head of security officer. External CCTV cameras to be IP rated
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-00-D-E-6841 Level 00 Security Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-00-D-E-6842 Level 00 Security Sheet 3
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-00-D-E-9001 Photovoltaic Canopies
P01 | 2025-03-14 | DFE Review | C - Rejected | 2025-04-01 | Details need to be updated with confirmed canopy sizes and direct reference to document containing full specification.
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-00-D-M-5210 Level 00 Above Ground Drainage Sheet 1
P02 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | 1. Consider relocating gully out of Cold Room, hygiene perspective 2. Main kitchen, no drains for combi ovens indicated on the drawing; Are we waiting for final kitchen layouts? 3. Numerous areas where pipework clashes with furniture; How is this to be resolved? 4. No high level pipe falls referenced
| 2025-04-07 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-00-D-M-5211 Level 00 Above Ground Drainage Sheet 2
P02 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | 1. Changing rooms indicate floor gully's, is this correct? No shower channels? 2. Numerous areas where pipework clashes with furniture; How is this to be resolved? 3. No high level pipe falls referenced 4. Can Condensate drains from HR007 / 008 & HR009 / 010 join together and connect to one Hepvo waterless trap?
| 2025-04-07 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-00-D-M-5212 Level 00 Above Ground Drainage Sheet 3
P02 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | WHB waste branch run too long, consider connection into WC float
| 2025-04-07 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-00-D-M-5310 Level 00 Domestic Water Services Sheet 1
P02 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | Minor comment - Food Rm - are services to drop within wall or on the surface (Clash with basin)
| 2025-04-07 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-00-D-M-5311 Level 00 Domestic Water Services Sheet 2
P02 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-00-D-M-5312 Level 00 Domestic Water Services Sheet 3
P02 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-00-D-M-5410 Level 00 Gas
P02 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-00-D-M-5610 Level 00 Heating and Cooling Sheet 1
P01 | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Valving arrangement is hard to read- would suggest numbering the typical details and refer to that, or removing entirely. 2. Plantroom drawing reference missing. 3. Symbol missing from Legend. PICV? 4. Should detail actual valve arrangement for underfloor heating (PICV and strainer missing)
| 2025-03-27 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-00-D-M-5611 Level 00 Heating and Cooling Sheet 2
P01 | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Symbol missing from Legend. PICV? 2. Should detail actual valve arrangement for underfloor heating (PICV and strainer missing)
| 2025-03-27 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-00-D-M-5612 Level 00 Heating and Cooling Sheet 3
P01 | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Symbol missing from Legend. PICV? 2. Should detail actual valve arrangement for underfloor heating (PICV and strainer missing)
| 2025-03-27 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-00-D-M-5710 Level 00 Ventilation Sheet 1
P02 | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Fire damper references are missing. 2. Comment that states 'Doesn't fit in CV' This should have been resolved at Stage 4. 3. Comment that states 'Fire damper requirements to be confirmed' This should be resolved at Stage 4. 4. Instances of intake and exhaust louvres being too close together. 5. Comment that states 'Coordination with ceiling to be resolved' This should have been resolved at Stage 4. 6. No access panels shown in ductwork for cleaning as per DW144
| 2025-03-27 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-00-D-M-5711 Level 00 Ventilation Sheet 2
P02 | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Fire damper references are missing. 2. Comment that states 'Doesn't fit in CV' This should have been resolved at Stage 4. 3. Instances of intake and exhaust louvres being too close together. 4. Review rationalising number of attenuators on extract ducts in changing rooms. 5. Comment that states 'Coordination with ceiling to be resolved' This should have been resolved at Stage 4. 6. No access panels shown in ductwork for cleaning as per DW144.
| 2025-03-27 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-00-D-M-5712 Level 00 Ventilation Sheet 3
P02 | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Fire damper references are missing. 2. Instances of intake and exhaust louvres being too close together. 3. Comment that states 'louvre doesn't fit' Should be resolved at Stage 4. 4. No access panels shown in ductwork for cleaning as per DW144
| 2025-03-27 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-00-D-M-5810 Level 00 Plantroom Sheet 1
P01 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-03-27 | 1. Has leak detection been fitted on drip tray over MCP
| 2025-03-27 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-00-D-M-5811 Level 00 Plantroom Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-00-D-Z-6010 Level 00 Builderswork Sheet 1
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-00-D-Z-6011 Level 00 Builderswork Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-00-D-Z-6012 Level 00 Builderswork Sheet 3
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-00-D-Z-9610 Level 00 Reflected Ceiling Plan Sheet 1
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-00-D-Z-9611 Level 00 Reflected Ceiling Plan Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-00-D-Z-9612 Level 00 Reflected Ceiling Plan Sheet 3
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-01-D-E-6110 Level 01 Containment Sheet 1
P01 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-02 | Containment has a number of branches in each classroom that are not similar to other classroom containment layouts
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-01-D-E-6111 Level 01 Containment Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-01-D-E-6210 Level 01 Small Power And Data Sheet 1
P01 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-02 | Is the amount of small power in the classrooms for the strudents confirmed as acceptable, there seems to be a lot of cable tray compared to other layouts.
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-01-D-E-6211 Level 01 Small Power And Data Sheet 2
P01 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-02 | "The 3No Comms racks have a mix of 16A and 32A supplies, please confirm this is correct. Is the amount of small power in the classrooms confirmed as acceptable, there seems to be a"
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-01-D-E-6212 Level 01 MSER Sheet 1
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-01-D-E-6213 Level 01 MSER Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-01-D-E-6310 Level 01 Lighting Sheet 1
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-01-D-E-6311 Level 01 Lighting Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-01-D-E-6810 Level 01 Fire Alarm Sheet 1
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-01-D-E-6811 Level 01 Fire Alarm Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-01-D-E-6820 Level 01 Fire Alarm Zoning Sheet 1
P01 | 2025-03-14 | DFE Review | C - Rejected | 2025-04-02 | Confirm if stairs will be these own zone as Ground level.
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-01-D-E-6821 Level 01 Fire Alarm Zoning Sheet 2
P01 | 2025-03-14 | DFE Review | C - Rejected | 2025-04-02 | Confirm if stairs will be these own zone as Ground level.
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-01-D-E-6840 Level 01 Security Sheet 1
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-01-D-E-6841 Level 01 Security Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-01-D-M-5210 Level 01 Above Ground Drainage Sheet 1
P02 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | 1. Numerous areas where pipework clashes with furniture; How is this to be resolved? 2. No high level pipe falls referenced 3. Waste traps from cleaners sinks are quite low, please confirm that it is able to connect into the common waste float
| 2025-04-07 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-01-D-M-5211 Level 01 Above Ground Drainage Sheet 2
P02 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | 1. Numerous areas where pipework clashes with furniture; How is this to be resolved? 2. No high level pipe falls referenced
| 2025-04-07 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-01-D-M-5310 Level 01 Domestic Water Services Sheet 1
P02 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-01-D-M-5311 Level 01 Domestic Water Services Sheet 2
P02 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-01-D-M-5410 Level 01 Gas
P02 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | 1. Rising 50 gas pipe in rm 01-1108 Art Rm clashing with furniture 01-6060c, this should be boxed in 2. Gas pipe passing through service riser 01-6060c, should this be pipe-in-pipe?
| 2025-04-07 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-01-D-M-5610 Level 01 Heating and Cooling Sheet 1
P01 | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Valving arrangement is hard to read- would suggest numbering the typical details and refer to that, or removing entirely. 2. Symbol missing from Legend. PICV?
| 2025-03-27 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-01-D-M-5611 Level 01 Heating and Cooling Sheet 2
P01 | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Valving arrangement is hard to read- would suggest numbering the typical details and refer to that, or removing entirely. 2. Symbol missing from Legend. PICV?
| 2025-03-27 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-01-D-M-5710 Level 01 Ventilation Sheet 1
P02 | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Comment that states 'Coordination with ceiling to be resolved' This should have been resolved at Stage 4. 2. GA clashes with legend- needs to be moved. 3. Confirm requirement of fire damper. 4. No access panels shown in ductwork for cleaning as per DW144.
| 2025-03-27 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-01-D-M-5711 Level 01 Ventilation Sheet 2
P02 | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Comment that states 'Coordination with ceiling to be resolved' This should have been resolved at Stage 4. 2. Louvres are too close together. 3. Confirm no requirement for fire dampers. 4. No access panels shown in ductwork for cleaning as per DW144
| 2025-03-27 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-01-D-Z-6010 Level 01 Builderswork Sheet 1
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-01-D-Z-6011 Level 01 Builderswork Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-01-D-Z-9610 Level 01 Reflected Ceiling Plan Sheet 1
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-01-D-Z-9611 Level 01 Reflected Ceiling Plan Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-02-D-E-6110 Level 02 Containment Sheet 1
P01 | 2025-03-14 | DFE Review | C - Rejected | 2025-04-02 | PV Submain route goes through the protected stair, is there an alternative or is this agreed?
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-02-D-E-6111 Level 02 Containment Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-02-D-E-6210 Level 02 Small Power And Data Sheet 1
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-02-D-E-6211 Level 02 Small Power And Data Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-02-D-E-6212 Level 02 MSER Sheet 1
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-02-D-E-6213 Level 02 MSER Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-02-D-E-6310 Level 02 Lighting Sheet 1
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-02-D-E-6311 Level 02 Lighting Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-02-D-E-6810 Level 02 Fire Alarm Sheet 1
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-02-D-E-6811 Level 02 Fire Alarm Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-02-D-E-6820 Level 02 Fire Alarm Zoning Sheet 1
P01 | 2025-03-14 | DFE Review | C - Rejected | 2025-04-02 | Confirm if stairs will be these own zone as Ground level.
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-02-D-E-6821 Level 02 Fire Alarm Zoning Sheet 2
P01 | 2025-03-14 | DFE Review | C - Rejected | 2025-04-02 | Confirm if stairs will be these own zone as Ground level.
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-02-D-E-6840 Level 02 Security Sheet 1
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-02-D-E-6841 Level 02 Security Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-02-D-M-5210 Level 02 Above Ground Drainage Sheet 1
P02 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | 1. Numerous areas where pipework clashes with furniture; How is this to be resolved? 2. Science lab sinks - dilution traps or pots?
| 2025-04-07 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-02-D-M-5211 Level 02 Above Ground Drainage Sheet 2
P02 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | 1. Pipework clashes with furniture; How is this to be resolved? 2. Waste traps from cleaners sinks are quite low, please confirm that it is able to connect into the common waste float
| 2025-04-07 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-02-D-M-5310 Level 02 Domestic Water Services Sheet 1
P02 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-02-D-M-5311 Level 02 Domestic Water Services Sheet 2
P02 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-02-D-M-5410 Level 02 Gas
P02 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | CO2 sensors are not indicated in rooms
| 2025-04-07 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-02-D-M-5610 Level 02 Heating and Cooling Sheet 1
P01 | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Valving arrangement is hard to read- would suggest numbering the typical details and refer to that, or removing entirely. 2. Symbol missing from Legend. PICV?
| 2025-03-27 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-02-D-M-5611 Level 02 Heating and Cooling Sheet 2
P01 | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Valving arrangement is hard to read- would suggest numbering the typical details and refer to that, or removing entirely. 2. Symbol missing from Legend. PICV?
| 2025-03-27 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-02-D-M-5710 Level 02 Ventilation Sheet 1
P02 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-02-D-M-5711 Level 02 Ventilation Sheet 2
P02 | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Comment that states 'Coordination with ceiling to be resolved' This should have been resolved at Stage 4. 2. Confirm requirement of fire damper. 3. No access panels shown in ductwork for cleaning as per DW144.
| 2025-03-27 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-02-D-Z-6010 Level 02 Builderswork Sheet 1
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-02-D-Z-6011 Level 02 Builderswork Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-02-D-Z-9610 Level 02 Reflected Ceiling Plan Sheet 1
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-02-D-Z-9611 Level 02 Reflected Ceiling Plan Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-RF-D-E-6213 Roof Level MSER
P01 | 2025-03-14 | DFE Review | C - Rejected | 2025-04-02 | "Cable contanment to Power supplies are not shown on a drawing, add note stating form of cable protection. Accronym list needs updating i.e. OD, HTU,LWH,GSV, EF,PSV etc"
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-RF-D-E-6810 Roof Level Fire Alarm Sheet 1
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-RF-D-E-6811 Roof Level Fire Alarm Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-RF-D-E-6840 Roof Level Security Sheet 1
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-RF-D-E-6841 Roof Level Security Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-RF-D-E-6842 Roof Level Security Sheet 3
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-RF-D-E-9001 Photovoltaic
P02 | 2025-03-14 | DFE Review | C - Rejected | 2025-04-01 | Details need to be updated to be consistent with latest design document and associated calculations used in energy modelling.
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-RF-D-M-5210 Roof Level Above Ground Drainage Sheet 1
P02 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-RF-D-M-5211 Roof Level Above Ground Drainage Sheet 2
P02 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-RF-D-M-5212 Roof Level Above Ground Drainage Sheet 3
P02 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-RF-D-M-5310 Roof Level Domestic Water Services Sheet 1
P02 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-RF-D-M-5311 Roof Level Domestic Water Services Sheet 2
P02 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-RF-D-M-5312 Roof Level Domestic Water Services Sheet 3
P02 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-RF-D-M-5710 Roof Level Ventilation Sheet 1
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-RF-D-M-5711 Roof Level Ventilation Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-RF-D-M-5712 Roof Level Ventilation Sheet 3
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-RF-D-Z-5810 Roof Level Plantroom Sheet 1
P02 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-RF-D-Z-5811 Roof Level Plantroom Sheet 2
P02 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-RF-D-Z-5812 Roof Level Plantroom Sheet 3
P02 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-RF-D-Z-6010 Roof Level Builderswork Sheet 1
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-RF-D-Z-6011 Roof Level Builderswork Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-RF-D-Z-6012 Roof Level Builderswork Sheet 3
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-D-E-9001 External Lighting
P04 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-02 | Contractor to confirm: No lighting under 2No of 3No PV Canopies and School Pitch and Games Court. External Luminaires are not in the luminaire schedule From Stage 3 comments (Item 20) Contractors response was that no external lighting was provided outside those on the final exits, due to there not being designated muster points. Has this been confirmed as acceptable with the Fire Engineer/Building Control.
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-XX-D-E-9002 External Lighting Lux Levels
P02 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-XX-D-E-9511 DNO Services Drawing and Proposal
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-XX-D-Z-5810 External Compound
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-D-Z-9510 External Services
P03 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-XX-L-E-0001 Proposed Manufacturers Electrical Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-XX-L-E-0002 Cable Calculation & Schedule Report
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-XX-L-E-0003 Containment Calculations
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-XX-L-E-0004 Lighting Calculations
P01 | 2025-03-14 | DFE Review | C - Rejected | 2025-04-02 | Assemby Hall achieving 300lux rather than 500lux. Servery not achieving 300lux. For Music Room and DT workshop, consider spacing the emergency lighting at edge rather than centre to improve the min emergency lighting level (currently under 0.5lux and 15lux) In Stage 3 comments (Item3) WSP asks for 200lux to lift as SLL code for lighting 200lux, confirm this has been calculated.
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-XX-L-E-0005 Exit Signage Calculation
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-XX-L-E-9602 Luminaire Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-XX-L-M-0003 Domestic Water Services Calculations
P01 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | HWSR no flow rate indicated in calcs
| 2025-04-07 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-XX-L-M-0004 Ventilation Calculations
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-0005 Gas Calculations
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-XX-L-M-0006 Above Ground Drainage Calculations
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-XX-L-M-0007 Heating Calculations
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-0008 Heat Source Calculations
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-9604 Heat Pump Schedule
P01 | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | Why N+1 for heating and 66% load per ASHP for DHW? (neither are incorrect). Should there be 7 units to provide N+1 according to your calculation?
| 2025-03-27 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-XX-L-M-9605 Buffer Vessel Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-9607 Plate Heat Exchanger Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-9608 Water Heater Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-XX-L-M-9609 Air & Dirt Separator Schedule
P01 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-03-27 | AD01 flowrate does not match schematic
| 2025-03-27 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-XX-L-M-9610 Dosing Pot Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-9613 Water Filter Schedule
P01 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-03-27 | Flowrate does not match schematic
| 2025-03-27 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-XX-L-M-9614 Water Softener Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-XX-L-M-9617 Leak Detection Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-9619 Gas Meter Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-XX-L-M-9620 Water Meter Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-XX-L-M-9621 Heat Meter Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-9623 Gas Solenoid Valve Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-XX-L-M-9624 Gas Detection & Proving Panel Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-XX-L-M-9625 Pressurisation Unit Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-9627 Storage Tank Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-XX-L-M-9628 Booster Set Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-XX-L-M-9630 Pump Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-9634 Local Water Heater Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-XX-L-M-9637 Radiator Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-9641 Underfloor Heating Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-9642 Underfloor Heating Manifold Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-9644 Overdoor Heater Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-9647 Electric Heater Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-9649 Fan Convector Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-9652 Air Handling Unit Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-9653 Heat Recovery Unit Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-9654 Hybrid Ventilation Unit Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-9655 Fan Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-9658 Louvre Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-9659 Supply Diffuser Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-9660 Extract Grille Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-9661 Attenuator Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-9662 Transfer Grille Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-9671 Heating Coil Schedule (LTHW)
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-9675 Smoke-activated Fire Damper Schedule
P01 | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | There are dampers missing that are shown on the layout but not on the schedule
| 2025-03-27 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-XX-L-M-9678 Passive Stack Ventilator Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-9681 DX Indoor Unit Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-M-9682 DX Outdoor Unit Schedule
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-L-Z-0001 Designers MEP Risk Assessment
P02 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-XX-L-Z-0004 Heat Loss Calculations
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-01 | No further comments
FS1018-AGL-ZZ-XX-T-E-0001 Electrical Specification
P01 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-02 | "Outstanding stage 3 comment WSP Comment:BS5839-1 says fire alarm sounder should not be used for purposes other than warning of fire, unless the response required is identical to that required in the event of fire (i.e immediate evacuation by use of all escape routes). However, as an established exception, the fire alarm signal may be used in schools to indicate start or finish of predetermined periods. The duration of such signal should not exceed 5s. Please confirm if the PA system and the class change system are independent of the fire alarm system. Responce: 'Discussions took place concerning the requirement of a class change system and the desired complexity involved regarding the PA system but no confirmation has been given. Current initial intention is to use the FA signal to indicate start or finish of classes, what is the schools desired preference?"
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-XX-T-E-0003 Electrical Maximum Demand
P02 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-02 | "Outstanding Stage 3 comment WSP Comment: Please confirm that the total power requirement for electric vehicle charging corresponds to the number of parking bays available on site. Check SoA for GIFA Responce: Assumed total power requirement for electric vehicle charging was based off 14No. Parking Spots (including disabled) outside the front of the school. WSP Current comment: there are currently 9no in the max demand, is this correct."
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-XX-T-M-0001 Mechanical Specification
P01 | 2025-03-14 | DFE Review | C - Rejected | 2025-04-01 | 1. Page 44. Number of ASHP contradicts schedule. 2. Page 51. Refers to DHW and not heating 3. Confirm ABS or MUPVC for small diameter waste pipes 4. Confirm if ABS or uPVC drainage stacks
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-XX-T-Z-0002 Plant Access Maintenance And Replacement Strategy
P02 | 2025-03-14 | DFE Review | C - Rejected | 2025-04-01 | 1. Document number does not match what is in the report. 2. MVHR- has access/access panels been coordinated with architect? 3. Confirm the access, maintenance, and replacement strategy for lighting and smoke detection systems in the assembly halls and sports hall.
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-XX-T-Z-0006 NBS Project Description
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-XX-T-Z-0007 Thermal Modelling, Compliance & Sustainability Report
P01 | 2025-03-14 | DFE Review | C - Rejected | 2025-04-01 | Need to ensure consistency with Solar PV modelling and make clear if IES modelled output is used in compliance calculations. Also need to update details to remove reference to Newcastle City Council - and ensure local planning guidance is accurate (as applicable to the current scheme).
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-ZZ-D-E-9001 Lightning Protection
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-ZZ-D-Z-6115 Server and Hub Room
P01 | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Where is the condensate drainage pipework?
| 2025-03-27 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-ZZ-D-Z-9610 Typical D&T Classroom
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-ZZ-D-Z-9611 Typical Food Room
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-ZZ-D-Z-9612 Typical ICT Classroom
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-ZZ-D-Z-9613 Typical Riser
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-ZZ-D-Z-9614 Typical Science Room
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-ZZ-G-E-6010 LV Schematic Sheet 1
P01 | 2025-03-14 | DFE Review | C - Rejected | 2025-04-02 | Breaker settings show allot of TBC. Please confirm that breaker to SB-02 (Way 25 on SB-01) discriminates with upstream device.
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-ZZ-G-E-6011 LV Schematic Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-ZZ-G-E-6811 Fire Alarm Schematic
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02
FS1018-AGL-ZZ-ZZ-G-M-5010 Controls Schematic
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-01
FS1018-AGL-ZZ-ZZ-G-M-5210 Above Ground Drainage Schematic Sheet 1
P01 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | 1. Remove stack vent detail 2. Relocate gully in Cold Room, hygiene perspective 3. Review cleaners sink waste connection; Cleaner sinks have low waste connections; Confirm that connection will connect to common waste float 4. There are single stub stacks with no top RE FW19 5. There are no Hepvo waterless traps indicated on the schematic for condensate drains.. 6. Can condensate units HR007/0008 waste join together? 7. Can condensate units HR009/010 waste join together?
| 2025-04-07 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-ZZ-G-M-5211 Above Ground Drainage Schematic Sheet 2
P01 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | 1. Remove stack vent detail 2. FG13 and add SH designation 3. Consider WHB 00-6018 & 00-6042a waste pipes connecting into the WC common float; Length of waste run looks too far from stack.
| 2025-04-07 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-ZZ-G-M-5310 Domestic Water Services Schematic
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 | (blank)
FS1018-AGL-ZZ-ZZ-G-M-5410 Gas Schematic
P01 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | 1. Level 00 gas entry, high and low level vent grilles, low level only indicated 2. No CO2 sensors indicated on the drawing
| 2025-04-07 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-ZZ-G-M-5610 Heating & Cooling Schematic Sheet 1
P01 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-03-27 | Appreciate flowrates, pipesizes etc are on the heating calculations document but would expect these to be on the schematic
| 2025-03-27 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-ZZ-G-M-5611 Heating & Cooling Schematic Sheet 2
P01 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-03-27 | Appreciate flowrates, pipesizes etc are on the heating calculations document but would expect these to be on the schematic
| 2025-03-27 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-ZZ-G-M-5612 Heating & Cooling Schematic Sheet 3
P01 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-03-27 | Appreciate flowrates, pipesizes etc are on the heating calculations document but would expect these to be on the schematic
| 2025-03-27 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-ZZ-G-M-5613 Heating & Cooling Schematic Sheet 4
P01 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-03-27 | Appreciate flowrates, pipesizes etc are on the heating calculations document but would expect these to be on the schematic
| 2025-03-27 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-ZZ-G-M-5710 Ventilation Schematic Sheet 1
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-ZZ-G-M-5711 Ventilation Schematic Sheet 2
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27
FS1018-AGL-ZZ-ZZ-G-M-5812 Plantroom Schematic
P01 | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-03-27 | CT HTG F&R flowrates don't align
| 2025-03-27 | Designer Response | Pending | (blank) | (blank)
FS1018-AGL-ZZ-ZZ-M-Z-0001 MEP Model Revit
P15 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-16
FS1018-AGL-ZZ-ZZ-M-Z-0002 MEP Model IFC
P15 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-16
FS1018-AGL-ZZ-ZZ-M-Z-0003 MEP Model NWC
P15 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-16
FS1018-CPM-XX-XX-L-A-0001 Schedule Of Accommodation
P06 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Please clarify why roof plant areas are included in the schedule. They are not internal spaces. 4.2 Proposed server room 2 is over area and the difference column has not been completed. Please clarify why this is over area. 4.3 Please clarify why the assembly hall is over the briefed area by 36m2. 4.4 Please clarify why GIFA is substantially over the briefed area
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-XX-XX-T-A-0005 Teaching Block Finishes
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Please indicate the DfE finishes references next to each item e.g. floor finish type F6.1 etc 4.2 This document makes reference to an IKO hot melt roof waterproofing system to all roof areas but section drawings refer to a Bauder system. Which one is correct? 4.3 Please indicate proposed RAL colours where currently stated TBC 4.4 Flooring indicated for showers is not suitable and dos not meet requirements of Technical Annex 2D. 4.5 Floor finishes do not match those indicated on floor finishes plans. Please coordinate the information. 4.6 Drinking fountain type does not meet the requirements of the DfE Output Specification 4.7 Please confirm that all sanitaryware meets the requirements of Technical Annex 2A 4.8 Outline spec refers to concealed cisterns but accessible WCs are indicated as having exposed cisterns. Please clarify
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-XX-XX-T-A-0010 Outline Specification
P09 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Elevations refer to three brick colours yet outline spec only refers to 'stone-buff colour.' Actual brick types not specified 4.2 Outline spec refers to darker engineering brick beneath DPC level but this is not indicated on the elevation drawings. Is the spec or drawing correct? 4.3 Curtain walling spec refers to triple glazing yet this is not shown on any drawings. Is this correct? 4.4 Section 3.0 Roof. Please confirm that the roof spec meets the following requirement of Technical Annex 2C... 3.4.1 External surfaces of roofs shall be EU Class B roof (T4) to ENV 1187 Part 4: external fire exposure classification. 4.5 Section 4.3 Sanitary Cubicles. Please confirm that doors meet the requirements of Technical Annex 2A… 3.2.3 Inward opening doors shall be able to open outwards through use of an emergency releasable door hinge or a lift-off facility to facilitate emergency assistance to someone who has fallen against the door inside the cubicle (blocking the door from opening). 4.6 Section 4.4 / 4.5. Please add a note to the outline spec to cover splashbacks to hand driers as per Technical Annex 2D 9.2.
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-XX-XX-T-A-5001 Stage 4 Report
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Section 1.07 community use plan diagram shows incorrect boundary of 'entrance zone 4.2 Section 6.04 shows 3d images of the main hall with lighting shown at what appears to be a low level not compliant with the minimum clear height requirements - please clarify. 4.3 Section 6.06 - image 9 is a repeat of image 3. 4.4 3D view in Section 8.03 shows mech vent clashing with glazing rather than meeting the louvred panel. 4.5 section 9.01 'accessible facilities' refers to clear circulation widths that are not actually achieved.
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-XX-XX-T-A-5002 Design Development Report
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-04 | 4.1 Document will require updating once stage 4 comments are addressed to pick up various issues
| 2025-04-04 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-XX-XX-T-A-5003 Pre-Construction Information
P01 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-CPM-XX-ZZ-L-A-0000 Building Model COBie Report
P25 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-16 | See Clarification for FS1018-MAJ-XX-XX-T-X-8001-AssetRegister-P02, On issued address new QC report needs to be issued. Please ensure that the Quality Control (QC) shows the output status for each COBie output reporting against the design criteria specified by the COBie schema
| 2025-04-16 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-00-D-A-2001 GA Proposed L00 Floor Plan
P17 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | note: drawing comments outstanding from stage 3 are numbered 3.x. New Stage 4 comments are numbered 4.x. 3.1 Review appropriateness of proposed kitchen layout and 4 spaces within. Locating them all to the north reduces the usable wall area for the kitchen layout. Also consider environmental health requirements for access to toilets an clean/dirty workstreams. Is it worth trying to cluster these uses either side of the external door? ...For example, to meet Food Hygiene Standards, a WC cannot be directly off food areas and therefore the WC needs to be separated off with an additional wall and door. 4.1 Door to Food Prep Room 1 needs to move over to avoid door furniture clashing with the column boxing as shown 4.2 Lockers not required. Please remove from the drawings/ FF&E. 4.3 Double doors to reception/ waiting area are shown as dual swing and clashing with corridor circulation. Please change to single swing so that they do not risk hitting persons in the main corridor. 4.4 Why are double doors to lobby 1 shown as dual swing? How does this work with the maglock/ access control strategy. We suggest changing to single swing open outwards. 4.5 Please confirm why the main entrance draught lobby has been increased in size to give access to the reception desk rather than the main reception desk being accessed via the waiting area 4.6 Please confirm why interview room 2 is not accessed from the secure lobby/ waiting area 4.7 Please indicate the required 465mm diameter standing space clear of the door swing as required by Approved Document T 4.8 Partition between music practice room and the main corridor does not meet the requirements of the Acoustic Report 4.9 How is the Control Room space accommodated in the plan?
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-00-D-A-2142 Ground Edge Details
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Please include a key for the line types/ colours 4.2 Detail 1 annotates rockwool insulation at 125mm but there is a stray dimension of 100mm. Please correct 4.3 Detail 1 text refers to SFS but no SFS is drawn 4.4 Detail 2. Please clarify how the gas membrane is detailed at the perimeter of the building. " 4.5 Detail 2. Structural drawings indicate a 250mm thick suspended RC slab yet this drawing indicates a slab thickness of on 205mm. Please coordinate a step in the slab to accommodate the sports floor if required. 4.6 Detail 3. Curtain walling bottom transom and cill not detailed correctly
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-00-D-A-2200 Wall And Partition Types L00
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Many of the wall type tags incorrectly annotate walls as having zero acoustic rating. 4.2 Partition between music practice room and the main corridor does not meet the requirements of the Acoustic Report
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-00-D-A-2900 Fire Strategy L00
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Please clarify the requirement for the fire exits to the sports hall internal store. Are these 2no. external doors required? They will be blocked by equipment most of the time. 4.2 Please confirm that the required clear opening widths of final exit doors are actually achieved with the doors proposed. The openings look too small in many cases
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-00-D-A-3001 External Door Schedules Sheet 01
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Please confirm that the required clear opening widths of final exit doors are actually achieved with the doors proposed. The openings look too small in many cases.
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-00-D-A-3050 Internal Doors Level 00 Sheet 01
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 The drawings do not indicate the correct method of measuring clear opening widths in accordance with diagram 9 of Part M volume 2
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-00-D-A-3051 Internal Doors Level 00 Sheet 02
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 The drawings do not indicate the correct method of measuring clear opening widths in accordance with diagram 9 of Part M volume 2
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-00-D-A-3052 Internal Doors Level 00 Sheet 03
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 The drawings do not indicate the correct method of measuring clear opening widths in accordance with diagram 9 of Part M volume 2
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-00-D-A-3053 Internal Doors Level 00 Sheet 04
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 The drawings do not indicate the correct method of measuring clear opening widths in accordance with diagram 9 of Part M volume 2 4.2 Odd push plates shown to the double door
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-00-D-A-3054 Internal Doors Level 00 Sheet 05
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 The drawings do not indicate the correct method of measuring clear opening widths in accordance with diagram 9 of Part M volume 2 4.2 Odd push plates shown to the double door
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-00-D-A-3500 Reflected Ceiling L00
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Drawing is difficult to read due to MEP items visible that should not be displayed in a reflected ceiling plan. Please amend for further review 4.2 Area of ceiling missing to gridline 3 around main entrance area 4.3 DT workshop ceiling rafts appear to clash with ceiling grid to the rear of the space 4.4 Key shows ceiling type C2.2 as blue hatch but the plan shows this as black. Please ensure the plan and the key correlate. Blue would be easier to see
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-00-D-A-6807 Room Elevations Hygiene Room
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Drawing shows exposed pipework. Technical Annex 2D requires concealed or tamperproof. Please confirm proposals 4.2 Please confirm how the falls are achieved to the gulley. Drawing shows a completely flat floor 4.3 Please remove or correct the 'floor finishes plan' which currently provides no information on floor finishes
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-00-D-A-6808 Room Elecations Pupil WC'S
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Drawing shows exposed pipework. Technical Annex 2D requires concealed or tamperproof. Please confirm proposals 4.2 Please remove or correct the ceiling plan which is unreadable at the moment. 4.3 Please remove or correct the 'floor finishes plan' which currently provides no information on floor finishes 4.4 Please indicate the required 465mm diameter standing space clear of the door swing as required by Approved Document T 4.5 Wash hand basin heights do not meet the height stated in Table 2 of Technical Annex 2A
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-00-D-A-6809 Room Elevations Pupils And Staff WC
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Drawing shows exposed pipework. Technical Annex 2D requires concealed or tamperproof. Please confirm proposals 4.2 Please remove or correct the ceiling plan which is unreadable at the moment. 4.3 Please remove or correct the 'floor finishes plan' which currently provides no information on floor finishes 4.4 Please indicate the required 465mm diameter standing space clear of the door swing as required by Approved Document T 4.5 Wash hand basin heights do not meet the height stated in Table 2 of Technical Annex 2A
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-00-D-A-6810 Room Elevations Accessible WC
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Drawing shows exposed pipework. Technical Annex 2D requires concealed or tamperproof. Please confirm proposals 4.2 Please remove or correct the ceiling plan which is unreadable at the moment. 4.3 Please remove or correct the 'floor finishes plan' which currently provides no information on floor finishes
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-00-D-A-6811 Room Elevations Changing Room
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Drawing shows exposed pipework. Technical Annex 2D requires concealed or tamperproof. Please confirm proposals 4.2 Please remove or correct the ceiling plan which is unreadable at the moment. 4.3 Please remove or correct the 'floor finishes plan' which currently provides no information on floor finishes 4.4 For WCs with doors opening inwards, please indicate the required 465mm diameter standing space clear of the door swing as required by Approved Document T 4.5 please add dimensions to the changing room benching so that the numbers of changing spaces can be reviewed. 4.6 Shower drainage currently indicates point drains to every other shower cubicle. This does not comply with the Technical Annex 2F section 12.2.9.3. 4.7 Drawings indicate that the shower cubicles are not full height. 4.8 Wash hand basin heights do not meet the height stated in Table 2 of Technical Annex 2A
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-00-D-A-6812 Room Elevations Accessible Changing Room
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Drawing shows exposed pipework. Technical Annex 2D requires concealed or tamperproof. Please confirm proposals 4.2 Please confirm how the falls are achieved to the gulley. Drawing shows a completely flat floor 4.3 Please remove or correct the 'floor finishes plan' which currently provides no information on floor finishes 4.4 Please remove or correct the ceiling plan which is unreadable at the moment. 4.5 Door requires a horizontal grab rail in accordance with diagram 23 of Part M.
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-01-D-A-2002 GA Proposed L01 Floor Plan
P16 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Medical Room is accessed off another room which is poor for pupil privacy. Please review 4.2 Please indicate clear width of all corridor spaces including alongside the light wells. 4.3 Please remove lockers. These are not to be supplied 4.5 Please review location of outward opening door the the accessible WC as the clear width of the corridor must not be affected by the door swing. 4.6 Please revise the view depth of the plan view so that the hall and sports hall are not indicated at this level. 4.7 Please confirm occupancy of the meeting room. It is a very large room for only 6 seats. 4.8 Façade setting out appears off as there is a thin section of brickwork alongside the window reveal to gridline S and 3 4.9 Door and FF&E not coordinated to Cleaners Store 3 4.10 Please add up arrows to all staircases
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-01-D-A-2201 Wall And Partition Types L01
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Many of the wall type tags incorrectly annotate walls as having zero acoustic rating.
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-01-D-A-2250 Patressing Plan For Typical Classroom
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 How does this comply with the pattressing requirement stated in Technical Annex 2D 3.1.1.f
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-01-D-A-2251 Patressing Plan For Art Room
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Patressing to elevation B misses the end of the wall mounted coat hooks
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-01-D-A-2901 Fire Strategy L01
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please annotate the evacuation lift 4.2 Lift car appears much larger than the minimum required by GDB 2.14.3.11 a. Please clarify 4.3 How does the fire strategy deal with the escape past the ventilation voids?
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-01-D-A-3501 Reflected Ceiling L01
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Drawing is difficult to read due to MEP items visible that should not be displayed in a reflected ceiling plan. Please amend to allow further review 4.2 Along gridline 5, classroom ceiling rafts appear to clash with ceiling grid/ tiles. 4.3 Key shows ceiling type C2.2 as blue hatch but the plan shows this as black. Please ensure the plan and the key correlate. Blue would be easier to see
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-01-D-A-6800 Room Elevations Classroom
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please remove or correct the ceiling plan which is unreadable at the moment. 4.2 Please remove or correct the 'floor finishes plan' which currently provides to no information on floor finishes 4.3 Please indicate dimension to underside of ceiling rafts 4.4 3D view indicates an exposed vertical pipework drop that clashes with a desk"
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-02-D-A-2003 GA Proposed L02 Floor Plan
P17 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please remove the visible steelwork to the assembly hall and to the sports hall roof areas. Assembly hall steel shows uncoordinated openings to roof vents. 4.2 Please indicate dimensions for clear width of corridors e.g. alongside the light wells and the appliance bay 4.3 For WCs, please indicate the required 465mm diameter standing space clear of the door swing as required by Approved Document T 4.4 Access to small group room looks very tight. Please review. Could the adjacent store be relocated to the alongside stair 4 at first floor level in a similar arrangement to the level 2 store alongside stairway 6.
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-02-D-A-2202 Wall And Partition Types L02
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Many of the wall type tags incorrectly annotate walls as having zero acoustic rating.
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-02-D-A-2902 Fire Strategy L02
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please annotate the evacuation lift 4.2 How does the fire strategy deal with the escape past the ventilation voids?
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-02-D-A-3502 Reflected Ceiling L02
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Drawing is difficult to read due to MEP items visible that should not be displayed in a reflected ceiling plan. Please amend to allow further review 4.2 Classroom ceiling rafts appear to clash with ceiling grid/ tiles to the rear of each space. 4.3 Key shows ceiling type C2.2 as blue hatch but the plan shows this as black. Please ensure the plan and the key correlate. Blue would be easier to see
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-RF-D-A-2023 GA Proposed Roof Plan
P15 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 PV panels are not indicated to the full extent of where they could be accommodated. The roof needs to be optimised for PV panels before external canopies can be justified. 4.2 Gravel fire breaks are not shown. Please refer to Technical Annex 2C 3.2.10 (f). 4.3 Further details of the roof escape hatch are required to confirm compliance with Technical Annex 2C section 3.6.
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-RF-D-A-2144 Roof Details Sheet 1
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please add levels/ dimensions to all upstands and parapets 4.2 Details annotate 'levelling screed' to the roof - is this the correct type of screed to use on a sloping roof? 4.3 No indication of wall ties
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-RF-D-A-2145 Roof Details Sheet 2
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Details annotate 'levelling screed' to the roof - is this the correct type of screed to use on a sloping roof? 4.2 Drawing is marked as 'preliminary' - please clarify why this is included for stage 4 review
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-RF-D-A-2903 Fire Strategy Rf
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please annotate each fire exit 4.2 Are sounders and or flashing beacons proposed at roof level? 4.3 PV panels on drawing and in the Key are different 4.4 Please indicate the gate to barrier around the rooflight means of escape as per Technical Annex 2C section 3.6
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-RF-D-A-3100 Rooflight Elevations Sheet 1
P01 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-03 | no comments
FS1018-CPM-ZZ-RF-D-A-3101 Rooflights And Hatch Plan
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 The key indicates that green dimensions are structural opening dimensions. For 1 and 2, how does the structure of each upstand work if the structure it outside of this as indicated i.e. how is the upstand structure supported
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-XX-D-A-2146 3D Section
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 The annotation refers to 100mm Knauf Rocksil Rainscreen Slab insulation with 50mm cavity but different insulation is indicated on other drawings (125mm Rockwool Nyroc with 25mm cavity) 4.2 Section through lift shaft does not indicate a lift pit or over-run. Are these not required?"
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-XX-D-A-2210 Partition Detail Plans
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Details 4, 8 and 10 show only 3 sides of column encased with BG Firecase. Does this detail provide the required fire protection for the steelwork? 4.2 Detail 4 is not detailed to mitigate sound transfer between rooms and goes against the guidance in diagram ADT 3567/SK1 of the Acoustic Report i.e. external wall linings cannot continue from one room to another as this allows noise transfer. 4.3 Detail 3. How does single layer of mineral wall insulation to the SFS work around the cross bracing as shown? 4.4 Details 5 and 11. Does this detail provide the required fire protection for the steelwork? 4.5 Detail 9. Insulation clashing with cross bracing.
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-XX-L-A-0020 CDM Design Risk Assessment
P03 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-0050 Circulation Strategy
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-04 | 4.1 Difficult to comment as not all dimensions are noted on the GA plans but in some cases the clear width indicated on this drawing (indicated in the key) does not match the actual clear width dimension indicated on the GA plan.
| 2025-04-04 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-0051 Zoning And Security Strategy
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Main entrance automatic doors, as referred to in the Outline Spec, not referenced on this plan. Security strategy needs to note this. 4.2 Access control is not shown to the double doors that lead from the main entrance waiting area into the main circulation corridor yet the two corridor doors are shown as having access control. Please clarify how the access control strategy allows visitors to wait in the waiting area without access to the corridor and the library. We suggest that the corridor access control is omitted and the access control required for the waiting area is added. 4.3 Doors that lead to roof access stairs and roof fire exit ladder are not shown as having a lock.
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-0052 Sanitary And Hygiene Strategy
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please indicate overall quantity of pupil WCs and overall quantity of staff WCs 4.2 Some drawings indicate the staff WC opposite the sick bay as being an accessible WC but this drawing shows it as not being accessible. Which is correct? 4.3 The layouts do not appear to comply with the handing requirements of Part M 5.10c. Please review
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-0053 Access And Maintenance Strategy
P05 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Hard standing area indicated around building perimeter is not actually provided on the landscape drawings 4.2 Please add a note to cover the maintenance strategy for non-accessible roof area over roof access stair 4.3 Please remove hatch to assembly hall and sports hall from the upper floors 4.4 Please list the kitchen fire shutter in section 4 of the scheduled tasks list
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-0054 Cleaning And Maintenance Strategy
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 3.1 How are smaller areas of roof proposed to be accessed, cleaned and maintained? Roofs to: LRC, Sports stores, entrance canopy For example: roof over access stair. Please strategy for gutter and outlet inspection and cleaning, plus visual inspection of roof. 3.2 Need to indicate access and clearances around roof plant / PV's, as well as travel distances
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-0060 Proposed Room Cluster Diagram
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-03 | no comments
FS1018-CPM-ZZ-ZZ-D-A-2001 GA Proposed Section Aa, Bb, Cc, Dd
P08 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 3.3 Please show proposed parapet levels to AOD 4.1 Main hall appears to show lighting compromising the clear height of the hall 4.2 Sections incorrectly show the topography as completely flat and level with internal FFL. 4.3 Clear height requirement for sports hall is not achieved.
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-2002 GA Proposed Section EE
P06 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Main hall appears to show lighting compromising the clear height of the hall 4.2 Section incorrectly shows the topography as completely flat and level with internal FFL. 4.3 Clear height requirement for sports hall is not achieved.
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-2010 GA Proposed Elevations Sheet 1
P08 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 3.1 Consider terminating curtain walling at half landing instead of running down to L00 level if this area under stair will be out of sight and inaccessible? Not best use of £ also consider robustness requirements of ER's (GDB and TA 2C) 4.1 are changing room doors proposed to be fully glazed? Consider the use of glazing film/ graphics/ signage to denote male and female changing rooms and also aid privacy 4.2 how is lighting over the main hall external doors going to be fixed to the glazing?" 4.3 Louvred panels to window system have very mixed appearance potentially caused my a clash from the MEP model 4.4 No brickwork movement joints indicated. 4.5 Are the glazed overpanels to sports hall store doors actually required?
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-2011 GA Proposed Elevations Sheet 02
P06 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 3.1 Consider terminating curtain walling at half landing instead of running down to L00 level if this area under stair will be out of sight and inaccessible? Not best use of £ also consider robustness requirements of ER's (GDB and TA 2C) 4.1 are changing room doors proposed to be fully glazed? Consider the use of glazing film/ graphics/ signage to denote male and female changing rooms and also aid privacy 4.2 how is lighting over the main hall external doors going to be fixed to the glazing? 4.3 Louvred panels to window system have very mixed appearance potentially caused my a clash from the MEP model 4.4 No brickwork movement joints indicated. 4.5 Are the glazed overpanels to sports hall store doors actually required? "
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-2012 GA Proposed Elevations Sheet 03
P05 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 3.1 Is signage on canopy sufficiently sized and contrasting for the person on the ground looking upwards? 4.1 Louvred panels to window system have very mixed appearance potentially caused my a clash from the MEP model 4.2 how is lighting over the main entrance external doors going to be fixed to the glazing? 4.3 No brickwork movement joints indicated.
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-2025 Hazard Identification Plan
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please indicate the working at height/ falls hazard of high level maintenance in hall spaces
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-2031 Internal Views
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Lighting to main hall is too low and impacts on the clear height requirement
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-2032 External Views
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 PV panels shown different in some views. Some are shown north facing. 4.2 Principal Entrance image shows ductwork clashing with louvred panels and lighting fixed to glass over main entrance doors.
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-2040 Lock Suiting Strategy
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Access control required to waiting area door to corridor but not likely to be required to the two sets of double doors within the corridor. Please clarify/ revise 4.2 Exam office and exam store shown on incorrect lock suite
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-2140 Construction Building Sections Sheet 1
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 3.1 Detail 2 (section B-B): Is there barrier matting here? 3.2 Are top hung opening light's automated? Or teleflex? 4.1 Section A-A shows top hung window in ceiling void 4.2 Levelling screed is not correct type of screed to lay on a sloping roof 4.3 Section B-B shows double glazed curtain walling but specification refers to trip glazing. 4.4 Section B-B annotates 'recessed concrete slab' to accommodate spring floor build up but this is not shown on the Structural Engineers information. Please coordinate 4.5 Levels not indicated for parapets 4.6 No mention of wall ties for brickwork outer leaf
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-2141 Construction Building Sections Sheet 2
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Does this height of brickwork require a shelf angle/ masonry support angle? 4.2 No mention of wall ties for brickwork outer leaf 4.3 Section shows a recess in the ground floor slab rather than a stepped slab. Neither a recess or a stepped slab are shown in the Structural Engineers information.
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-2143 External Wall Details Sheet 1
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 How is fire protection to the steelwork achieved?
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-2144 External Wall Details Sheet 2
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 How is fire protection to the steelwork achieved?
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-2401 Typical Staircase Sheet 01
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please confirm that the curtain walling system achieves the actual clear opening width required for the final exit
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-2402 Typical Staircase Sheet 02
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 bottom landing for roof access stair is less than the stair width. Does this meet Part K requirements
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-2403 Typical Staircase Sheet 03
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 How are the exposed steel beams and the back of the curtain walling spandrel panels proposed to be finished?
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-2404 Typical Staircase Sheet 04
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 How are the exposed steel beams and the back of the curtain walling spandrel panels proposed to be finished?
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-2405 Typical Staircase Sheet 05
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 How are the exposed steel beams and the back of the curtain walling spandrel panels proposed to be finished? 4.2 How are the handrails supported alongside the curtain walling?
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-3002 External Door Schedues Sheet 02
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Some door types have structural opening widths and or heights that are not brick dimensions. How does this work?
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-3010 Curtain Wall Panelling Elevations Sheet 01
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Curtain wall B has a structural opening height that is not a brick dim. How does this work?
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-3011 Curtain Wall Panelling Elevations Sheet 02
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Curtain wall E has a structural opening height and width that is not a brick dim. How does this work?
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-3020 External Windows Elevation And Schedule
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Is window type 04 actually used? The schedule suggests not 4.2 Is window type 03 clear glazing for the server room? Does this create unwanted solar gain and potential overheating issues? 4.3 Schedule for window type 5 is off the page 4.4 Cill heights in schedules refer to 900mm but there is a stray red dimension of 1050mm that is noted as 'sill height' - is this actually the glazing height. Please clarify 4.5 Do high level opening windows have a teleflex?
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-3021 Internal Glazed Panel Elevations And Schedule
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please clarify the design intent for glazed screen type 06? What it’s the purpose of this and how does it work with the servery fire shutter? 4.2 What are the fire and acoustic requirements?
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-3055 Internal Doors Level 00 Sheet 06
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 The drawings do not indicated the correct method of measuring clear opening widths in accordance with diagram 9 of Part M volume 2
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-3062 Window Schedule
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Structural opening dimensions are not all brick dims. How does this work?
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-4001 GA Wall Finishes Strategy
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please specify wall finishes for the spaces currently noted as 'contractor to specify' 4.2 Please clarify the proposal for wall finish type W3.2. The key refers to a brush applied finish but also refers to a 'Hygenik H Panel' and an eggshell paint finish 4.3 Please clarify the proposed finishes to the hygiene room and the changing rooms/ showers. The key refers to ceramic tiling to showers but does not define the extent 4.4 Does the catering kitchen/ food prep room comply with Technical Annex 2D paragraph 9.1.23 4.5 Please add a key to explain the blue dashed lines. If these are to denote splashbacks, please confirm that they meet Technical Annex 2D section 9.2. 4.6 Please include proposals for wall finishes to the corridor light wells. The wall finishes would need to match the corridors but the plans currently just state 'n/a' 4.7 Sports hall acoustic wall finishes appear to measure 2400mm in height and are set 2400mm from FFL. Please clarify that this follows the recommendations of the acoustician as the Acoustic Strategy Report refers to perforated panels from FFL up to 3000mm height. 4.8 Both the wall types and wall finishes plans do not show how the exam store complies with JCQ requirements for security measures. Please refer to GDB 2.3.19.2
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-4004 GA Floor Finishes Strategy
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please confirm the proposals for floor type F6.1 i.e. timber or vinyl top surface/ A3 or A4 area elastic rating/ product and thickness 4.2 Please confirm the proposals for floor type F6.2h i.e. timber or vinyl top surface/ A3 or A4 area elastic rating/ product and thickness 4.3 Please confirm proposals for the flooring currently noted as 'contractor to specify' 4.4 Please clarify the proposals for floor type F7.3h noting that the text currently in the key would result in non-compliant flooring to the changing rooms/ showers 4.5 Please confirm proposals for the flooring currently noted as 'contractor to specify' 4.6 Please remove the colour from the roof areas, MEP risers and light wells as this is misleading 4.7 Please clarify the proposals for skirting. This drawings states pencil round skirting but External Wall details show chamfered. 4.8 Please confirm floor finishes proposals for the lift and stairs. 4.9 Please confirm how and why the floor finish works to the 'control room' within the bleacher seating area 4.10 Please confirm how the two areas are barrier matting are incorporated in the assembly hall floor finish 4.11 Please add barrier matting to the 2no. external doors to the stair cores at ground floor level 4.12 Please confirm product proposed for barrier matting 4.13 Please review rooms where there is a transition in floor finish i.e. pastoral room and SENCo office at first floor level, staff work room at second floor level and ground floor premises office and proposed one floor finish. To be raised as a derogation to be agreed.
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-6601 Lift Pit Details
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Lift car is oversized compared to the DfE minimum size required by GDB 2.14.3.11 a. Please clarify 4.2 Is a lift over-run required? 4.3 Is the liftshaft blockwork actually being design by a specialist subcontractor as noted on the drawing? 4.4 Is the lift shaft blockwork actually constructed off the screed as drawn? 4.5 Are two forms of waterproofing proposed for the lift pit? To achieve a Grade 3 environment 4.6 The 'ground edge details' indicate a gas membrane. How is the detailed around the lift pit?
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-6801 Room Elevations Assembly Dining Sheet 1
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please remove or correct the ceiling plan which is unreadable at the moment. 4.2 Please remove or correct the 'floor finishes plan' which currently provides to no information on floor finishes 4.3 Lighting indicated in the 3d image is too low and conflicts with the minimum clear height requirement 4.4 Please clarify how access to the lighting and audio controls unit can be accessed. Looks like it is not accessible both when the bleacher seating is in use and also when the bleacher seating is not in use.
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-6802 Room Elevations Assembly Dining Sheet 2
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Lighting to main hall is too low and impacts on the clear height requirement 4.2 Exposed pipework along gridline 6A 4.3 How is the air curtain unit fixed. Can this be coordinated with the exposed steelwork so that the air curtains have something to fix to, the pipework could be boxed out and the steelwork hidden on the outside with a spandrel in the curtain walling 4.4 Radiator positions appear to clash with bleacher seating
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-6803 Room Elevations Sports Hall Sheet 1
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please add dimensions to the court markings setting out 4.2 Please indicate the location of the rooflights on the ceiling plan and annotate the items 4.3 Is the sports hall lighting over the badminton courts rather than in between the courts 4.4 In reality will the cricket nets clash with the basketball back board as drawn?
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-6804 Room Elevations Sports Hall Sheet 2
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Floor finishes plan provides no information on floor finishes. Is this drawing required being as there is a separate floor finishes plan intended to provide information on floor finishes? 4.2 3D view indicates clash between dividing curtain and what looks like containment / cable tray.
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-6805 Room Elevations Sports Hall Sheet 3
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please add a key for the location of each section. 4.2 Please move section 3 so that each room elevation displays properly. This appears to show the cricket nets on gridline S. Fire exit doors on gridline Y are not visible. 4.3 The drawing indicates clash between dividing curtain and what looks like containment / cable tray. 4.4 Section 4. Can the first floor glazed screen line up with the door below? 4.5 Clear sports hall height of 7500mm has not been achieved. Currently obstructed by steelwork and MEP
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-6806 Room Elevations Sports Hall Acoustic Panel Set Out
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please mark the elevations on the plan" 4.2 How does the panelling work around doors? No doors are indicated 4.3 Extent of acoustic panels does not match the acoustic report recommendations
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-D-A-6813 Room Elevations Pupil WC'S L01 And L02
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Floor finishes plan provides no information on floor finishes. Is this drawing required being as there is a separate floor finishes plan intended to provide information on floor finishes? 4.2 Please indicate the required 465mm diameter standing space clear of the door swing as required by Approved Document T 4.3 Drawings appear to show 2no. hand dryers per WC. One at high level 4.4 Reflected ceiling plan is not readable 4.5 Wash hand basin heights do not meet the height stated in Table 2 of Technical Annex 2A
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-L-A-0001 Clash Report
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 The report identifies 560 pages of clashes but contains no information on the proposed remediation or 'owners' of each clash.
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-L-A-3060 Internal Door Schedule
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Schedule goes off the page. Is part of it missing? 4.2 Please clarify the difference between the ratings and performance
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-L-A-3061 External Door Schedule
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please clarify why some doors are noted as requiring a 30min fire rating and 30dB acoustic rating 4.2 Structural opening dimensions are not all brick dims. How does this work?
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-M-A-0002 Federated Model
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-16 | Not all disciplines models have been intergratd into the Federated Model (catering & Civil)
| 2025-04-16 | Designer Response | Pending | (blank) | (blank)
FS1018-CPM-ZZ-ZZ-M-A-0003 Architectural Model NWC
P25 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-16
FS1018-CPM-ZZ-ZZ-M-A-0004 Architectural Model IFC
P25 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-16
FS1018-CPM-ZZ-ZZ-M-A-0005 Architectural Model Revit
P25 | 2025-04-09 | DFE Review | A - Accepted | 2025-04-16
FS1018-CPM-ZZ-ZZ-V-A-0001 External Flythrough Video
P01 | 2025-03-14 | DFE Review | A - Accepted | 2025-04-03 | no comments
FS1018-CPM-ZZ-ZZ-V-A-0002 Internal Flythrough Video
P01 | 2025-03-14 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Various comments picked up elsewhere in the drawings pack. For example, hall lighting clashes with clear height requirements, odd pushplates to some doors, some pinboards clashing with dado trunking, ceiling rafts clashing with ceiling grid.
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-EVR-XX-XX-D-O-0001 Server Room Location
P03 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-EVR-XX-XX-D-O-0002 ICT Plans
P03 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-EVR-XX-XX-D-O-0003 Wireless Heat Maps
P01 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-EVR-XX-XX-D-O-0004 Server Cabinet Layout
P01 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-EVR-XX-XX-G-O-0001 ICT Network Diagrams
P02 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-EVR-XX-XX-L-O-0001 ICT Equipment List
P02 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-EVR-XX-XX-L-O-0002 ICT Cost Matrix
P02 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-EVR-XX-XX-L-O-0003 ICT Small Power and Data Schedule
P01 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-EVR-XX-XX-L-O-0004 ICT Construction Programme
P02 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-EVR-XX-XX-T-O-0002 ICT Calculations
P01 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-EVR-XX-XX-T-O-0004 ICT Contractor's Proposals
P01 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-EVR-XX-XX-T-O-0005 Post Award ICT Meetings (PAM) Agendas
P01 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-EVR-XX-XX-T-O-0006 User Acceptance Testing (UAT) Schedule
P01 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-EVR-XX-XX-T-O-0007 Post Award ICT Meetings (PAM) Minutes
P01 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-D-X-0001 Site Construction Plan
P01 | 2025-03-26 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-D-X-0003 Site Set Up Plan Phase 1
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-19 | this document shows the correct car park layouts for this phase. therefore can FS1018-HBC-XX-XX-D-X-0001 be removed?
| 2025-03-26 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-D-X-0004 Site Set Up Plan Phase 2 Section 1
P02 | 2025-03-26 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-D-X-0005 Site Set Up Plan Phase 2 Section 2
P01 | 2025-03-26 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-D-X-0006 Site Set Up Plan Phase 3
P01 | 2025-03-26 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-L-X-0001 MIDP
P15 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-L-X-0003 Design Programme
P02 | 2025-03-26 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-L-X-0004 Construction Programme
P02 | 2025-03-26 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-L-X-0005 Master Programme
P02 | 2025-03-26 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-L-X-0006 Works Package Procurement Programme
P02 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-L-X-0007 Risk Register
P02 | 2025-03-26 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-L-X-0008 PCSA
P02 | 2025-03-28 | DFE Review | A - Accepted | 2025-04-01 | (blank)
FS1018-HBC-XX-XX-L-X-0009 PCSA Milestone Schedule
P02 | 2025-03-28 | DFE Review | A - Accepted | 2025-04-01 | Standard milestone PCSA payment schedule.
FS1018-HBC-XX-XX-L-X-0010 PCSA Certificate Of Completion
P02 | 2025-03-28 | DFE Review | A - Accepted | 2025-03-31 | (blank)
FS1018-HBC-XX-XX-L-X-0011 Cashflow Forecast
P02 | 2025-04-01 | DFE Review | A - Accepted | 2025-04-01 | Construction cashflow included.
FS1018-HBC-XX-XX-L-X-0012 Framework Pricing Schedule
P03 | 2025-03-28 | DFE Review | C - Rejected | 2025-03-31 | A1 Cost summary sheet. The sums entered do not match nor total correctly. The whole schedule needs to be reviewed by contractor and QA correctly.
| 2025-04-10 | DFE Review of Responses | C - Rejected | 2025-04-10
P04 | 2025-04-10 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-L-X-0013 DFE KPIs
P02 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-L-X-0014 Supplier Directory CV
P03 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-L-X-0016 Handover Training Plan
P02 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-L-X-0018 HB Social Value KPIs
P02 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-L-X-0019 Site Organisation Chart
P01 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-L-X-0020 Commissioning Programme
P01 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-L-X-1001 Quality Management Plan
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 | (blank)
FS1018-HBC-XX-XX-L-X-1002 Sustainable Estate Strategy
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | Details need updating throughout to reflect current design proposal.
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-L-X-1003 Lift Specification
P01 | 2025-03-26 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-L-X-1004 Project Execution Plan
P02 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-L-X-3000 Derogations Schedule
P05 | 2025-04-17 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-L-X-4000 Planning Condition Tracker
P01 | 2025-03-26 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-T-X-0001 Construction Phasing Plan
P03 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-T-X-0012 Cost Plan Summary
P01 | 2025-04-10 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-T-X-0024 CEM7 Meeting Minutes
P01 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01
FS1018-HBC-XX-XX-T-X-0025 CEM8 Meeting Minutes
P01 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01
FS1018-HBC-XX-XX-T-X-0026 CEM8-9A Meeting Minutes
P01 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01
FS1018-HBC-XX-XX-T-X-0027 CEM09 Meeting Minutes
P01 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01
FS1018-HBC-XX-XX-T-X-0028 CEM10 Meeting Minutes
P01 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01
FS1018-HBC-XX-XX-T-X-0029 CEM10A Meeting Minutes
P01 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01
FS1018-HBC-XX-XX-T-X-0030 CEM11 Meeting Minutes
P01 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01
FS1018-HBC-XX-XX-T-X-0031 CEM12 Meeting Minutes
P01 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01
FS1018-HBC-XX-XX-T-X-0033 CEM07 Agenda
P01 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01
FS1018-HBC-XX-XX-T-X-0034 CEM08 Agenda
P01 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01
FS1018-HBC-XX-XX-T-X-0035 CEM09 Agenda
P01 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01
FS1018-HBC-XX-XX-T-X-0036 CEM08-9A Agenda
P01 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01
FS1018-HBC-XX-XX-T-X-0037 CEM10 Meeting Agenda
P01 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01
FS1018-HBC-XX-XX-T-X-0038 CEM10A Agenda
P01 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01
FS1018-HBC-XX-XX-T-X-0039 CEM11 Agenda
P01 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01
FS1018-HBC-XX-XX-T-X-0040 CEM12 Agenda
P01 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01
FS1018-HBC-XX-XX-T-X-0042 Employer Necessary Consents
P01 | 2025-03-26 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-T-X-0043 Construction Method Statement
P01 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-T-X-0044 Handover Strategy
P01 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-HBC-XX-XX-T-X-0045 Thermal Assessment
P01 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 | (blank)
FS1018-HEX-XX-XX-T-C-0004 Civil Design Philosophy
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-25 | D1 3. Geo-Environmental notes groundwater risk - drainage design is sealed/lined to prevent groundwater ingress and will not therefore not reduce groundwater around the structure. Geotechnical input required. D2 4. No flooding information provided as part of this submission - condition, water levels within watercourse, overland flow routes. Risk of back flow when water level in culvert is high. D3. 5. Status of Internal Drainage Board (IDB) approval to be confirmed as it will affect the design requirements. D4 5. Works are proposed within 9m of the watercourse culvert. Constructability risk that will need to be managed and agreed with IDB - Foundation and drainage installation. Pre and post construction survey of the culvert may be necessary D5 5. It has been noted that additional survey is required to determine existing drains, condition and levels. At this stage we would expect survey works to be complete especially for location and levels of outfalls. D6 6. It has been noted that additional design may be necessary following engagement with IDB and flow rates are yet to be agreed. Therefore the Stage 4 Technical Design is not complete. D7 6. Specialist manufacturer design is still required for storage tanks. Proposed tank depth does not reflect manufacturer storage units, shallow depth of cover, flotation risk and proximity to structure are all risks to be managed within the storage tank design. D8 7. Foul design is yet to be agreed with Anglian Water, location and levels to be confirmed D9 9. Has a timeline for outstanding surveys, design and approvals been agreed? Extent of survey, repairs to existing network, specialist design, conditions/redesign are significant risks. D10 Information available does not include: hydraulic analysis results treatment strategy Emergy shutoff and containment in the eventof a fire ot pollution event to protect downstream watercourse. profiles connection details specialist design elements - linear drains, storage tank
| 2025-03-25 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-XX-XX-T-C-0010 Risk Register
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-25 | Consider adding approvals, additional requirements from IDB, surcharged outfall, pollution control/emergency shutoff and remaining design/reliance on specialist designers
| 2025-03-25 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-XX-XX-T-C-0011 Drainage Specification
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-25 | 1. Geotextile and geomembrane specification requirements and testing to be confirmed. 2. Confirm if non-return and emergency shutoff valves are required. 3. Confirm any specialist drainage signage required. 4. Specialist design requirements may need to be included when available.
| 2025-03-25 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-XX-XX-T-C-0012 Earthworks Specification
P01 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-HEX-XX-XX-T-H-0001 Transport Assessment
P02 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-HEX-XX-XX-T-S-0003 Structural Design Philosophy
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Please refer to comments at the end of the uploaded file.
| 2025-03-28 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-XX-XX-T-S-0004 Concrete Specification
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Please review in light of other comments.
| 2025-03-28 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-XX-XX-T-S-0005 Steelwork Specification
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28
| 2025-03-28 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-XX-XX-T-S-0006 Piling Specification
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Please review in light of other comments.
| 2025-03-28 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-ZZ-00-D-S-0101 Foundation Layout
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28
| 2025-03-28 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-ZZ-00-D-S-0102 Foundation Details
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28
| 2025-03-28 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-ZZ-00-D-S-0200 Ground Floor Column Plan
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Typical design intent for column base plates/ HD arrangement must be shown in section and plan for each column type and for columns at the separation joint. Some beam levels in staircase still to be confirmed. Overall lateral stability strategy is not clear qualitatively. Lost of bracing is concentrated in the sports hall but very few braced bays in the main building. Vertical braces not doubled up along the separation joint on GL - D1/E. In the sports hall there is a significant amount of glazed elevation but no bracing - are any connections that are intended to be moment resisting?
| 2025-03-28 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-ZZ-01-D-S-0201 First Floor Steelwork Layout
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Please review in light of other comments, particularly overall stability/bracing, separation joints/ movement joints etc. Is there an intention for a separation joint along GL - S?
| 2025-03-28 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-ZZ-02-D-S-0202 Second Floor Steelwork Layout
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Please review in light of other comments, particularly overall stability/bracing, separation joints/ movement joints etc. Is there an intention for a separation joint along GL - S?
| 2025-03-28 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-ZZ-RF-D-S-0203 Main Roof Steelwork Layout
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Please review in light of other comments, particularly overall stability/bracing, separation joints/ movement joints etc. Is there an intention for a separation joint along GL - S?
| 2025-03-28 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-ZZ-RF-D-S-0204 Hall Roof Steelwork Layouts
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Please review in light of other comments, particularly overall stability/bracing, separation joints/ movement joints etc. Is there an intention for a separation joint along GL - S?
| 2025-03-28 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-ZZ-RF-D-S-0205 Parapet Steelwork Layout
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Please review in light of other comments.
| 2025-03-28 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-ZZ-XX-D-S-0001 Project Notes
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Piling Notes - Reference to precast piles? Piling Notes - Piling Specification appears incomplete - Provide a full Project Specification covering all relevant aspects from Section B1 of ICESPERW Piling Notes - Is 500mm anchorage sufficient? What bar diameter is this to be? Structural Steelwork Notes - Project Specification should be reviewed against NSSS Section Checklists and all relevant items included. Structural Steelwork Notes - Connection loads not available Structural Masonry Notes - typical indicative details for masonry should be included on drawings to supplement these notes.
| 2025-03-28 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-ZZ-ZZ-D-C-5200 Surface Water Drainage Layout Sheet 1
P05 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-25 | 1. Due to the size and shape of tank there is a risk of ponding within the tank. Designer and Manufacturer to consider fall across the tank so it can drain out. 2. Tank Depth of cover = 0.73 could be difficult to get a manufacturers design as they generally specify 0.9 - 1.2m minimum. 3. clash and constructability risk between building and storage tank 4. Potential constructibility risks within and adjacent to IDB maintenance strip to be considered - piling, drainage, plant movement, vibration and loading adjacent to culvert 5. Outfall connection - Confirm downstream pipe size, may require access point (SSG) rather than a saddle connection to existing. 6. As surface water drainage is sealed to prevent ingress from groundwater. Can we confirm that this has been communicated and taken into account for the structure design. Geotech and Structures to confirm. 7. Acute angle <90deg between incoming and outgoing pipes. 8. Terminology could be confusing - is Private proposed or an existing asset belonging to others?
| 2025-03-25 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-ZZ-ZZ-D-C-5201 Surface Water Drainage Layout Sheet 2
P05 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-25 | See comments for sheet FS1018-HEX-ZZ-ZZ-D-C-5200
| 2025-03-25 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-ZZ-ZZ-D-C-5205 Foul Water Drainage Layout
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-25 | 1. Depth, size and gradient of underfloor pipes to be confirmed to ensure there is no clash with foundation and chamber connections can be achieved. Groundwater risk to pipe connections 2. Gully connection to FW1a has shallow cover which may affect performance and constructability 3. Outfall location, levels and condition will need to be confirmed to prove connection. 4. Legend - Existing SW sewer linetype scale is not clear. 5. Terminology could be confusing - is Private proposed or an existing asset belonging to others?
| 2025-03-25 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-ZZ-ZZ-D-C-5210 Drainage Construction Details Sheet 1
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-25 | 1. Details refer to SFA 7th Edition rather than SSG. 2. orifice plate - size, material, thickness and connection requirements required. 3. text missing from orifice chamber detail. 4. wrapping filter drains with impermeable membrane will prevent water in/out. if the aim is to prevent ingress/infiltration then it should state 'trench to be lined with impermeable membrane to prevent ingress of groundwater'. 5. Extent of geotextile is not clear. Geotextile will be required between sand and aggregate. 6. Surface water plans appear to show dry swales (TBC) A detail will be required.
| 2025-03-25 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-ZZ-ZZ-D-C-5211 Drainage Construction Details Sheet 2
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-25 | 1. storage crate units are typically 400 - 500mm high which doesn't fit with 0.74m depth of tank. 2. Catchpit - Additional details required: Brick, mortar, steps. Are weep pipes proposed for draining lower trench bedding? 3. Swale comments: Swale side slope should be shown as 1:3 Max. A dry swale detail is required? Is there a max water depth, freeboard or base width? Longitudinal slopes TBC Liner and geotextile not clear due to line thickness, scale and adjacent hatching. 4. Additional details may be required such as rodding eye, RWP connection, linear drain outlet and siphonic break chamber.
| 2025-03-25 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-ZZ-ZZ-D-C-9000 Earthworks Analysis
P01 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-HEX-ZZ-ZZ-D-C-9020 External Works Layout Sheet 1
P02 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-HEX-ZZ-ZZ-D-C-9021 External Works Layout Sheet 2
P02 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-HEX-ZZ-ZZ-D-C-9025 External Works Construction Details
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-25 | Permeable block paving - consider nominal fall across geomembrane to ensure water doesn't become perched.
| 2025-03-25 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-ZZ-ZZ-D-S-0501 Building Elevations Sheet 01 Of 02
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Please review in light of other comments, particularly overall stability/bracing, separation joints/ movement joints etc. Is there an intention for a separation joint along GL - S?
| 2025-03-28 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-ZZ-ZZ-D-S-0502 Building Elevations Sheet 02 Of 02
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Please review in light of other comments, particularly overall stability/bracing, separation joints/ movement joints etc. Is there an intention for a separation joint along GL - S?
| 2025-03-28 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-ZZ-ZZ-D-S-0503 Bracing Elevations
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Please review in light of other comments, particularly overall stability/bracing, separation joints/ movement joints etc. Is there an intention for a separation joint along GL - S?
| 2025-03-28 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-ZZ-ZZ-D-S-0601 Building Sections
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Detail of roof build-up and framing of roof lights and vents not available. Some vertical members shown in blue on Section - 3-3, what are these? Does the main roof rafter not need any stays/restraints in uplift? No details available.
| 2025-03-28 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-ZZ-ZZ-D-S-0602 Structural Sections and Details
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Please review in light of other comments, particularly overall stability/bracing, separation joints/ movement joints etc. Is there an intention for a separation joint along GL - S? Tying of hollow core to steelwork - can 4x slots be formed in a 200 the hollo core slab? The bearing of hollow core slab on beams appears small - confirm bearing length. Due to chamfer of hollo core slabs has the potential of hollow core shearing off been considered in the temporary stage? No detail for precast staircase foundation and its connection. No details of any barriers/handrails etc. Design intent of masonry supports/curtain walling not clear with the details presented. Notes re Co-ordination TBC should be removed at this stage. Tall parapets - no connection intent detail available. What type of connections are intended generally - no details available. Detail through riser beam - open section used - has this beam been designed for torsion. The bearing plate outstand appears large - has this been adequately designed? Potential of instability with hollow core planks in construction stage should be added as a residual CDM risk on all relevant drawings. No CDM design risk register available. Has precambered effect on dead/screed loads been considered? No vertical and plan bracing connection intent provided.
| 2025-03-28 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-ZZ-ZZ-D-S-0801 3D Views
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Please review in light of other comments, particularly overall stability/bracing, separation joints/ movement joints etc. Is there an intention for a separation joint along GL - S?
| 2025-03-28 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-ZZ-ZZ-M-C-0001 Native Civil Model
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-16 | Issued on Splash sheet as S3, please ensure when it's issued for Acceptance it's in S5 status. Miss Alignment of model in splash sheet
| 2025-04-16 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-ZZ-ZZ-M-C-0002 IFC SPF Civil Model
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-16
FS1018-HEX-ZZ-ZZ-M-C-0003 Navisworks Civil Model
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-16
FS1018-HEX-ZZ-ZZ-M-S-0001 Native Structural Model
P09 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-16 | Issued on Splash sheet as S1 for coordination, please ensure when it's issued for Acceptance it's in S5 status
| 2025-04-16 | Designer Response | Pending | (blank) | (blank)
FS1018-HEX-ZZ-ZZ-M-S-0002 IFC SPF Structural Model
P09 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-16
FS1018-HEX-ZZ-ZZ-M-S-0003 Navis Structural Model
P09 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-16
FS1018-HEX-ZZ-ZZ-T-C-0001 General Notes
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-25 | Drainage Notes: 13. No protection slab detail provided 14. three week appication for Section 106 is a programme and approval risk. Survey and design to be completed prior to application 16. BS EN 295 current standard is 2013. Confirm strength for pipes 150 - 300 as the requirement appears to be 48kN/m Pavement - Geotechnical and pavement risks appear to be passed on to site. Cost, programme risk and responsibility TBC Pavement Notes: 4. Geotechnical and pavement risks appear to be passed on to site. Cost, programme risk and responsibility TBC 5. Should there be an instruction here for testing results to be provided, timescale and design updated accordingly. 6. Works decisions being passed on to site which could bypass the design and review process, Who makes the determination and who takes responsibility? Kerbing notes: Spelling to be checked to reduce confusion.
| 2025-03-25 | Designer Response | Pending | (blank) | (blank)
FS1018-MAJ-XX-XX-L-X-0090 Detailed Responsibility Matrix
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-16 | Does not indicated when the information is to be exchanged and with whom; and which task team is responsible for its production. As per ISO 19650‑2:2018 5.4.2
| 2025-04-16 | Designer Response | Pending | (blank) | (blank)
FS1018-MAJ-XX-XX-L-X-8001 Asset Register
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-11 | Ensure the colours of the columns used in the 05_Alphanumerical_COBieFields and refer to PIS for naming conventions Facility Tab - Created by NumberOfStoreys & UPRN marked as N/A require details. Floor - Please Correct Name floor convention from 00 to Level 00 Space - Name -naming convention is incorrect - See PIS 5.2.5 Space Nomenclature for correct naming convention. Created by, Category , Floor Name, Zone - Created by , Space name incorrect , Type - Created by , Category, description, asset type, NominalLength, NominalWidth, NominalHeight ,PredefinedType incorrect Component - Name , Created by ,Space, InstallationDate, WarrantyStartDatein correct System - Name , Category ,ComponentNames,Description
| 2025-04-11 | Designer Response | Pending | (blank) | (blank)
FS1018-MAJ-XX-XX-L-X-8002 COBie QC Report
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-16 | See Clarification for FS1018-MAJ-XX-XX-T-X-8001-AssetRegister-P02, On issued address new QC report needs to be issued. Please ensure that the Quality Control (QC) shows the output status for each COBie output reporting against the design criteria specified by the COBie schema
| 2025-04-16 | Designer Response | Pending | (blank) | (blank)
FS1018-MAJ-XX-XX-T-X-0001 BIM Execution Plan
P06 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-16 | AllDiscipline Models need to listed in the BEP All Federated models and models incorprated in Federated model needs to be listed in BEP ALL MIDP and TIDP 's need to be listed in BEP 9.6 Classification - Update as per PIS 4.5.1 Asset Classification 9.10 Maximum File Size - please update BIM file sizes as many of the models are larger than 300MB 9.11 Volume and model division - 9.11 Volume and model division 10.4 Volume Code (Field 3) - Building Volume code as per Project Information Standard 5.1.4 Functional Breakdown Codes 11.1 COBie Workbooks Required - Add Instruction Workbook required 11.6 COBie Data Zones and Zoning Naming - not matching the Project information standards 5.2.6 Zone Nomenclature
| 2025-04-16 | Designer Response | Pending | (blank) | (blank)
FS1018-MAJ-XX-XX-T-X-1001 Information Managers Report
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-16 | Report needs to be done against models issued with submission. Report submitted on older revision of models
| 2025-04-16 | Designer Response | Pending | (blank) | (blank)
FS1018-MAJ-ZZ-ZZ-M-X-0001 Federated Information Model
P06 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-11 | Arch,MEP, FFE not matching IFC iisued. Also not listed on BEP so can't confirm namign conventions. See Asset register lcarifications for COBie data issues Landscape model trees misaligned
| 2025-04-11 | Designer Response | Pending | (blank) | (blank)
FS1018-OFR-XX-ZZ-G-K-0001 Fire Strategy Report
P05 | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | 1. In Section 5 of the fire strategy, add the justification of the services riser being located within 'Stair 2' within 'Table 6', for the attention of building control. 2. (Table 15) Has the fire service been consulted with regards to the requirements needed for the load bearing capacity of the roads for the fire vehicle used to attend the site in an emergency? As it will affect the civil engineer's design.
| 2025-03-31 | Designer Response | (HB Only) Comments Acknowledged | 2025-04-04 | OFR Response: 1. Section 5 - Fire Strategy (Table 6) The service riser is located within the lobby rather than within Stair 2. As this design aligns with standard guidance, it does not constitute a deviation and therefore is not included in Table 6. OFR Response: 2. Table 15 - Fire Service Access Response: OFR has outlined the design expectations for fire vehicle access, including load-bearing capacity and dimensional requirements, as detailed in Table 15. These specifications should be adopted by the civil engineer to ensure compliance. HEXA Civil Engineer response: 2. Table 15-Fire Service Access The fire tender access to the site was considered in the development of the pavement build-ups, and as such the build-ups in the areas that anticipate access by a fire tender has been designed accordingly.
| 2025-04-04 | DFE Review of Responses | Pending | (blank) | (blank)
FS1018-ONE-XX-XX-T-L-0001 Outline Specification
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-02 | The document does not have the level of detail expected at RIBA stage 4, please provide full specifications for each of the items listed, i.e. for the litter bin, please provide the make and model, the fixings to be used and confirmation of the colour.
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-ONE-XX-XX-T-L-0002 Design Development Schedule
P02 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-ONE-XX-ZZ-D-L-0001 Location Plan
P05 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-03
FS1018-ONE-XX-ZZ-D-L-0002 Existing Site Plan
P07 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-03
FS1018-ONE-XX-ZZ-D-L-0003 Whole Site Plan
P14 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 3.1 please indicate the proposals for the existing storage container 3.2 awaiting proposals for location of kerb-side refuse store 4.1 Areas of landscaping to the perimeter of the building clash with the hardstanding area noted on the architectural drawings required for maintenance of the building. 4.2 Please change the colour for the proposed trees vs existing trees, as mentioned many times, it is difficult to tell the difference. 4.3 Please confirm the status of the tree in the most northern swale, in the TCA car park, as it has a red dotted line to imply that it is being removed but it is also green, which implies it is new – this can not occur as it would be over a drainage pipe. 4.4 Tree over drainage pipe adjacent to parking space 129. 4.5 Please coordinate the drainage plan with the landscaping plans as there are a number of swales on the eastern side of the building which are either shown at different sizes, or not shown at all. Example south of parking bay 16 to the top of the turning head. 4.6 The drainage plan implies that there will be a swale adjacent to the rear of the dining terrace, please confirm if this is correct. 4.7 Please be consistent with fence line colouring. Also, please clarify where the 2.4m high fencing is proposed
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-ONE-XX-ZZ-D-L-0004 Site Landscaping Plan 1 of 5
P07 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 3.1 please indicate the proposals for the existing storage container 3.2 awaiting proposals for location of kerb-side refuse store "4.1 Areas of landscaping to the perimeter of the building clash with the hardstanding area noted on the architectural drawings required for maintenance of the building. " "4.2 Please indicate the gate swing of the existing site access gates. It looks like the proposed pedestrian crossings will clash with the gates when in the open position. " "4.3 Do the refuse collection strategy and the catering delivery require a dropped kerb alongside the service bay to allow for wheeled bins and deliveries trolleys?" 4.4 Please check the level indicator arrows on the pedestrian path from Weasenham Lane. 4.5 Please confirm what the blue bubble to the west of the dining terrace is for?
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-ONE-XX-ZZ-D-L-0005 Site Landscaping Plan 2 of 5
P07 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "3.1 please indicate the proposals for the existing storage container" "3.2 awaiting proposals for location of kerb-sied refuse store" "4.1 Please clarify what the hatched area is to the left of the existing storage container"
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-ONE-XX-ZZ-D-L-0006 Site Landscaping Plan 3 of 5
P07 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "3.1 please indicate the proposals for the existing storage container" "4.1 Areas of landscaping to the perimeter of the building clash with the hardstanding area noted on the architectural drawings required for maintenance of the building. " "4.2 Please clarify what the hatched area is to the left of the existing storage container" 4.3 Please confirm what the blue bubble to the west of the building is for?
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-ONE-XX-ZZ-D-L-0007 Site Landscaping Plan 4 of 5
P07 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 SuDs area is simply coloured and labelled as SuDs in the key. Please indicate the proposals?" 4.2. Please confirm if root protection is actually required for all of the trees on the south east boundary. 4.3. Please review the colouration of the EV charging parking bays as they appear to be shown as Existing Permeable Concrete Block Retained, which is not correct.
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-ONE-XX-ZZ-D-L-0008 Site Landscaping Plan 5 of 5
P07 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 SuDs area is simply coloured and labelled as SuDs in the key. Please indicate the proposals?" "4.2 Please indicate the fence proposals around the sub-station"
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-ONE-XX-ZZ-D-L-0009 Access and Security Strategy
P08 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 Please indicate the fence proposals around the sub-station"
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-ONE-XX-ZZ-D-L-0010 Circulation Strategy
P06 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 What is the strategy for providing access and parking for the sub-station? How is this compliant with GDB 2.8.1.14 and raise as a derogation if necessary" "4.2 Please add white lining for an additional crossing lining up with northernmost accessible parking bay and running east to the parking space to the eastern run of parking bays."
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-ONE-XX-ZZ-D-L-0011 External Sports Provision
P07 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 Please indicate the access points for both TCA and WFS for accessing any shared sports provision"
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-ONE-XX-ZZ-D-L-0012 Green Infrastructure Plan
P08 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | Need to confirm if green roof is being included or not and extent of it soo that UGF calculation is complete.
| 2025-04-01 | Designer Response | Pending | (blank) | (blank)
FS1018-ONE-XX-ZZ-D-L-0013 BB103 Guidance
P05 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 Please indicate the red line boundary along with the area within the red line boundary." "4.2 Please indicate the historic figures for comparison i.e. control option/ stage 3"
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-ONE-XX-ZZ-D-L-0014 Hazard Identification Plan
P06 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 Are there no construction related risks with sharing site access with the temporary school?" "4.2 Are there no hazards relating to enabling works/ highways works for section 1.0?"
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-ONE-XX-ZZ-D-L-0015 Refurbishment Remodelling Strategy
P09 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 extent of hard landscaping does not match up with the architectural information - specifically please coordinate the hard standing to the building perimeter for maintenance access." 4.2 Further coordination needed with Portakabin regarding the parking area for Wisbech Free School.
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-ONE-XX-ZZ-D-L-0017 Site Sections
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 unable to access the information via Aconex" "4.2 Pedestrian crossings near entrance gates, tactile paving and dropped kerbs are incorrectly shown as areas with no work. "
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-ONE-XX-ZZ-D-L-0021 Existing Site Plan 1 of 5
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-03
FS1018-ONE-XX-ZZ-D-L-0022 Existing Site Plan 2 of 5
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-03
FS1018-ONE-XX-ZZ-D-L-0023 Existing Site Plan 3 of 5
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-03
FS1018-ONE-XX-ZZ-D-L-0024 Existing Site Plan 4 of 5
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-03
FS1018-ONE-XX-ZZ-D-L-0025 Existing Site Plan 5 of 5
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-03
FS1018-ONE-XX-ZZ-D-L-0201 Detailed Planting Plan Sheet 1 of 5
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 Soft landscaping clashes with the hard standing zone for maintenance access to the building perimeter shown on the architectural drawings" 4.2 Please coordinate the drainage plan with the landscaping plans as there are a number of swales on the eastern side of the building which are either shown at different sizes, or not shown at all. Example south of parking bay 16 to the top of the turning head.
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-ONE-XX-ZZ-D-L-0202 Detailed Planting Plan Sheet 2 of 5
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 How is the habitat area defined in terms of planting?"
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-ONE-XX-ZZ-D-L-0203 Detailed Planting Plan Sheet 3 of 5
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 Soft landscaping clashes with the hard standing zone for maintenance access to the building perimeter shown on the architectural drawings"
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-ONE-XX-ZZ-D-L-0204 Detailed Planting Plan Sheet 4 of 5
P03 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-03
FS1018-ONE-XX-ZZ-D-L-0205 Detailed Planting Plan Sheet 5 of 5
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Shrubs should not be planted in the swale to the north of the TCA car park.
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-ONE-XX-ZZ-D-L-0401 Outline Levels Plan 1 of 5
P07 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-03
FS1018-ONE-XX-ZZ-D-L-0402 Outline Levels Plan 2 of 5
P07 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-03
FS1018-ONE-XX-ZZ-D-L-0403 Outline Levels Plan 3 of 5
P07 | 2025-03-13 | DFE Review | A - Accepted | 2025-04-03
FS1018-ONE-XX-ZZ-D-L-0404 Outline Levels Plan 4 of 5
P06 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 Please indicate levels proposals for the swale"
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-ONE-XX-ZZ-D-L-0405 Outline Levels Plan 5 of 5
P06 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 Please indicate levels proposals for the swale"
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-ONE-XX-ZZ-D-L-0601 Landscape Details Sheet 1
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 Section 2 has the curved part of the canopy structure missing"
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-ONE-XX-ZZ-D-L-0602 Landscape Details Sheet 2
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Lack of information on the foundation detail.
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-ONE-XX-ZZ-D-L-0603 Landscape Details Sheet 3
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 Please indicate the type of timber cladding proposed"
| 2025-04-03 | Designer Response | Pending | (blank) | (blank)
FS1018-ONE-ZZ-XX-T-L-0004 Security Statement
P02 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-ONE-ZZ-ZZ-M-L-0001 Landscape Model
P03 | 2025-04-14 | DFE Review | A - Accepted | 2025-04-14
FS1018-ONE-ZZ-ZZ-M-L-0002 Landscape Model
P03 | 2025-04-14 | DFE Review | A - Accepted | 2025-04-14
FS1018-ONE-ZZ-ZZ-M-L-0003 Landscape Model
P03 | 2025-04-14 | DFE Review | A - Accepted | 2025-04-14
FS1018-PIN-XX-XX-L-O-0003 Task Team Risk Register
P02 | 2025-03-13 | DFE Review | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-0001 Ground Floor GA 1 Of 2
P05 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Update based on review comments.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-0002 Ground Floor GA 2 Of 2
P05 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Update based on review comments.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-0006 Lobby 1
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1. Can a detailed drawing of the reception hatch reception be provided?
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-0601 Food Prep Area, Kitchen Servery And Wash Up 1
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Spur shelving 2 tier racking, impeding access to external double doors. 2.Hand wash station should be closer to external doors. 3.Can the office area be accessed or form part of the off dry store to reduce number of doors and free up walls/dead space in kitchen area. 4.Door swing to cold room is missing of drawing. 5. What is the servery and hot/cold provision sufficient for number of pupils moving through? "
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-1109 Music Room
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Only space for 14 keyboards allowed, should this be 15? Could the store room door be moved toward window to allow for an additional keyboard. 2. 2.Can the DDA desk to be one of the desks that face the whiteboard?
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-1110 DT Workshop 1
P05 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Is there sufficient circulation space between machines and desks. 2. Please add dimensions to all equipment 3. Can the desk layout be better utilised, perhaps rotating the desks 45 degrees so pupils don’t have their back to the whiteboard. With the DDA desk better located near the whiteboard and the teacher not with their back to one of the benches?
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-1111 Food Room 1 Option 1
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1. Can the desk be moved to the end and rotated to face the whiteboard, with another circulation for access? 2.Can the handwash be moved from behind the door? 3.Can an extra sink be included here? 4. These sections are not reflective of the floor plan
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-1112 DT Studio Graphic Products
P07 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.The classroom does not accommodate the 28 pupils as per the school request.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-1113 DT Studio Electronics And Control
P07 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Can the DDA desk be moved to face the whiteboard, with enough circulation space to access?
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-1211 Food Room 1
P05 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1. Is the DDA kitchen compliant with prep space required next to the hob area -600mm? 2. The DDA desk is not near the DDA kitchen, can this be relocated? 3. Does the hand sink need to be directly behind the door, can this be switched with coat hooks? 4. Currently there is central cluster of 3x hobs with no sinks, can these be better distributed?
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-2001 Assembly Hall, Dining Layout
P07 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-07 | Seating capacity is listed as 138 but shows seating for 144. As all pupils need to be seating for lunch, please indicate how this is achieved within the lunch time period and the current seating provided. If more tables are required, can this be accommodated?
| 2025-04-07 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-2002 Sports Hall Exam Layout
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Please update the store room layout to current layout provided.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-2003 Assembly Hall, Assembly Layout
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-07 | 1.Please demonstrate the SOA capacity in the drawing? 2. Can the refrigerated servery units be relocated when not in use? 3.Where are the chairs being stored when not in use, not shown in drawings?
| 2025-04-07 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-3002 Sports Hall Sport Layout
P05 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-00-D-O-3004 LRC
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Can the floor swing be flipped and the door be moved to the right to improve circulation in the space?
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-4003 Enclosed Office, Admin Head 1
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Is there potential to switch seating and desk area, to avoid glare from the the window?
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-4004 Enclosed Office, Admin PA 1
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-00-D-O-4005 Reprographics Room 1
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-00-D-O-4006 Enclosed Office, With Recep Desk And Window 1
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Can more space be provided to the desks at the reception desk , taken from the row behind?
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-4008 Reception Area, Entrance 50% Circulation
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Rejected, due to concerns raised around the arrangement of the secure line, furniture layout may need to be change.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-4009 Confidential Meeting Room Interview 1
P03 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-00-D-O-4015 Office With Meeting Area, 2 Person 4
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | One of the walls is missing from the drawing, please can you update so that it is clear.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-4018 Staff Workroom Premises 1 And Equipment Store, Maintenance 1
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-00-D-O-5003 Confidential Meeting Room Interview 1
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Rejected, due to concerns raised around the arrangement of the secure line, furniture layout may need to be change.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-5007 DT Prep Room 1
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-00-D-O-5008 Food Prep Room 1
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-00-D-O-5009 Teaching Resources Store Off DT Studio
P03 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-00-D-O-5011 Teaching Resources Store Off DT Studio
P03 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-00-D-O-5013 Teaching Resources Store Music 1
P03 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-00-D-O-5018 Sports Equipment Store, Internal Sports Hall 1
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-00-D-O-5019 Sports Equipment Store, External 1
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-00-D-O-5103 Secure Storeroom 1
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-00-D-O-5109 Coats And Bag Store Lockers 1
P03 | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Appreciate the trust has specifically removed these. Please indicate on each locker drawing the location of the lockers and quantity of lockers that could be provided in that area if later required, with the overall number of lockers also listed for reference.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-5114 Cleaners Store
P03 | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Update title to cleaners store 1
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-5117 Cleaners Store
P03 | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Update title to cleaners store 4
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-6001 Dining And Catering
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Has a noticeboard been provided (BOA001) 2. The refrigerated servery are located away from he canteen.Is there an agreed plan of how pupils queue and move through the canteen space. 3.Are 3x tills required and should two of the tills sit back to back to provide better circulation, there is a column in front of the first till.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-6002 Office, Kitchen 1
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Can the office area be accessed or form part of the off dry store to reduce number of doors and free up walls/dead space in kitchen area.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-6003 Food Store, Kitchen Dry 1
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Can the office area be accessed or form part of the off dry store to reduce number of doors and free up walls/dead space in kitchen area.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-6004 Cold Store, Kitchen 1
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | SOA is 2.5m2 however door to freezer reduces useable space
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-6005 Cold Store, Kitchen Freezer 1
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Incorrect drawing. Needs updating to reflect new design.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-6006 Toilet (With Changing Area) 1
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1. Toilet should be separate from the changing area, 2.The COSHH cabinet should be located elsewhere.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-6007 Changing Room, With Showers Pupils 1 And Toilets, Suite Pupils, Other 1
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Update GA to reflect 2. Does the occupancy allow for 38 pupils as per the SOA. It appears only 33 have been allowed for. It appears there is sufficent space to add extra benching to come closer to the SOA requirement of 38. 3. Can circulation space be dimensioned including shower area to enable us to review?
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-6008 Changing Room, With Showers Pupils 2 And Toilets, Suite Pupils, Other 2
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Update GA to reflect 2. Does the occupancy allow for 38 pupils as per the SOA. It appears only 33 have been allowed for. It appears there is sufficent space to add extra benching to come closer to the SOA requirement of 38. 3. Can circulation space be dimensioned including shower area to enable us to review?
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-6009 Music Practice Room 2
P04 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-00-D-O-6011 Hygiene Room 1
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-00-D-O-6042 First Aid Post Sick Bay 1 And Stairway 7
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-00-D-O-6069 Circulation Space Horizontal On And Coats And Bag Store Lockers 1
P02 | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Appreciate the trust has specifically removed these. Please indicate on each locker drawing the location of the lockers and quantity of lockers that could be provided in that area if later required, with the overall number of lockers also listed for reference.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-7001 Dining And Catering 3D
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Commented on separate drawings. Please revise.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-7003 Dishwashing
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Can the door better be located to improve circulation space, due to location of tills? This comment forms part of multiple other comments around the kitchen layout and design.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-7101 Food Prep Area, Kitchen Servery And Wash Up 1 Electrical Plan
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-02 | Isolators required for full height fridges, as isolation not accessible
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-7201 Food Prep Area, Kitchen Servery And Wash Up 1 Electrical Elevations
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-02 | Isolators required for full height fridges, as isolation not accessible
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-7301 Food Prep Area, Kitchen Servery And Wash Up 1 Mechanical Plan
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-02 | 1. No section lines for elevations 2. There is no drinking water, cold water is from a boosted cold water system, see AGL drawings 3. Service drops to whb on grid line 3A / B are in correct refer to AGL water / drainage drawings 4. Misspelling of tundish 5. Supply to to water boiler on AGL drawings indicate 15 and no 22 6. Unit clashing with doorway 7. AGL services to adjust to new appliance location 8. Floor gully (G), who is positioning the gully? AGL or Pinnacle?
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-7401 Food Prep Area, Kitchen Servery And Wash Up 1 Mechanical Elevations
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-02 | 1. Pinnacle services are not in the correct location, refer to AGL Services drawings and are clashing with the doorway. 2. AGL Services are required to be extended to new sink location 3 AGL Services are required to be adjusted to new sink location 4. Unit clash with doorway 5. Misspelling of tundish 6. There is no drinking water, cold water is from a boosted cold water system, see AGL drawings 7. How is grease managed? If there is a grease trap, who is supplying the grease trap?
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-7501 Dishwash Services Requirements
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-04-02 | 1.AGL services are to be adjusted to suite new unit locations 2.How is grease managed? If there is a grease trap, who is supplying the grease trap? Dishwasher and combi ovens 3.Floor gully (G), who is positioning the gully? AGL or Pinnacle? Table clashing with gully
| 2025-04-02 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-8001 Music Practice Room 1
P04 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-00-D-O-8003 Music Practice Room Extensive 1
P04 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-00-D-O-9001 Classroom Store, Room Off Sen Room 1
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | SOA is 5m2, 3.28m2 provided.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-00-D-O-9003 Teaching Resources Store Music 2
P03 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-01-D-O-1000 First Floor GA 1 Of 2
P05 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-01-D-O-1001 First Floor GA 2 Of 2
P05 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Update based on review comments. 2. Is water fountain would be better located between office and SEN room?
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-01-D-O-1002 Classroom General 2
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | No DDA desk shown. Add desk spacing dims.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-01-D-O-1003 Classroom General 3
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | No DDA desk shown. Add desk spacing dims.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-01-D-O-1004 Classroom General 4
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Add desk spacing dims.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-01-D-O-1005 Classroom General 5
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | No DDA desk shown. Add desk spacing dims.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-01-D-O-1006 Classroom General 6
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | No DDA desk shown. Add desk spacing dims.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-01-D-O-1007 Classroom General 7
P05 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Add desk spacing dims.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-01-D-O-1008 Classroom General 8
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | No DDA desk shown. Add desk spacing dims.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-01-D-O-1009 Classroom General 9
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | No DDA desk shown. Add desk spacing dims. .
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-01-D-O-1021 Classroom General 1
P05 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Add desk spacing dims.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-01-D-O-1101 ICT Rich Classroom 1
P06 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Can the middle bank of desk be moved 200cm towards the door to allow for better circulation?
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-01-D-O-1102 ICT Rich Classroom 2
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Can you relocate the DDA desk to the centre bank of desk, so they do not have their back to the whiteboard? 2.Can you rotate the teacher's desk to face door?
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-01-D-O-1108 Art Room General
P05 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-01-D-O-3006 Medical Treatment Mi Room 1 And 3007 Sen Resource Space 1
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Not ideal to access medical room off the SEN room, potential switch with staff workroom?
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-01-D-O-3009 Small Group Room Large Sen Etc. 1
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Can DAA desk be moved to the other end of the desk bank and dimensions added to demonstrate adequate circulation is provided
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-01-D-O-4002 Meeting Room Conference 1
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1. What is proposed occupancy? Is the room area too large for the requirements or is the FF&E provision too little.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-01-D-O-4007 Office Pastoral 1 And 5002 Teaching Resources Store It Gt Off Corridor 2
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Is this the most appropriate layout, tall shelving near the window, I think a better layout can be achieved.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-01-D-O-4012 Office With Meeting Area, 2 Person 1
P04 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-01-D-O-4013 Office With Meeting Area, 2 Person 2
P04 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-01-D-O-4016 Office Senco, Learning Support 1
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Can the layout of the this room with the classroom store near the window be improved?
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-01-D-O-4017 Staff Workroom ICT Technicians 1
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Tambour unit is against a window
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-01-D-O-5006 Teaching Resources Store Off Art Room 1
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-01-D-O-5017 Classroom Store, Room Off Sen Room 1
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Can the layout of the this room with the classroom store near the window be improved. Doesn't seem the most logical use of space and daylight.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-01-D-O-5104 Secure Storeroom 2
P03 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-01-D-O-5110 Coats And Bag Store Lockers 2
P03 | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Appreciate the trust has specifically removed these. Please indicate on each locker drawing the location of the lockers and quantity of lockers that could be provided in that area if later required, with the overall number of lockers also listed for reference.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-01-D-O-5111 Coats And Bag Store Lockers 3
P03 | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Appreciate the trust has specifically removed these. Please indicate on each locker drawing the location of the lockers and quantity of lockers that could be provided in that area if later required, with the overall number of lockers also listed for reference.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-01-D-O-5112 Coats And Bag Store Lockers 4
P03 | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Appreciate the trust has specifically removed these. Please indicate on each locker drawing the location of the lockers and quantity of lockers that could be provided in that area if later required, with the overall number of lockers also listed for reference.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-01-D-O-5113 Coats And Bag Store Lockers 5
P03 | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Appreciate the trust has specifically removed these. Please indicate on each locker drawing the location of the lockers and quantity of lockers that could be provided in that area if later required, with the overall number of lockers also listed for reference.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-01-D-O-5116 Cleaners' Store 3
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-02-D-O-1010 Classroom General 10
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Add desk spacing dims.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-02-D-O-1011 Classroom General 11
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | No DDA desk shown. Add desk spacing dims.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-02-D-O-1012 Classroom General 12
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | No DDA desk shown. Add desk spacing dims.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-02-D-O-1013 Classroom General 13
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | No DDA desk shown. Add desk spacing dims.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-02-D-O-1014 Classroom General 14
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Add desk spacing dims.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-02-D-O-1015 Classroom General 15
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | No DDA desk shown. Add desk spacing dims.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-02-D-O-1016 Classroom General 16
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Add desk spacing dims.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-02-D-O-1042 6042P Stairway 7 And 5113A Coats And Bag Store Lockers 5
P03 | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Appreciate the trust has specifically removed these. Please indicate on each locker drawing the location of the lockers and quantity of lockers that could be provided in that area if later required, with the overall number of lockers also listed for reference.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-02-D-O-1103 Science Laboratories Restrictive, Extg 1
P05 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | No DDA desk shown. Add desk spacing dims.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-02-D-O-1104 Science Laboratories Restrictive, Extg 2
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | No DDA desk shown. Add desk spacing dims.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-02-D-O-1105 Science Laboratories Restrictive, Extg 3
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Can DDA face the whiteboard. Add desk spacing dims.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-02-D-O-1106 Science Laboratories Restrictive, Extg 4
P04 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Add desk spacing dims.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-02-D-O-1107 Science Laboratories Restrictive, Extg 5
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Can DDA face the whiteboard. Add desk spacing dims.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-02-D-O-2000 Second Floor GA
P05 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Update based on comments 2. Is the water fountain the best location near busy door ways, can this be located near the office with less traffic. Office door be more centrally placed.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-02-D-O-2042 6042O Stairway 7 And 5113B Coats And Bag Store Lockers 5
P03 | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Appreciate the trust has specifically removed these. Please indicate on each locker drawing the location of the lockers and quantity of lockers that could be provided in that area if later required, with the overall number of lockers also listed for reference.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-02-D-O-3008 Small Group Room Medium 1 And 6042T Stairway 7
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Should seating for 6 puplils be provided not 2.Add desk spacing dims
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-02-D-O-3042 6042N Stairway 7, 5113C And 5113D Coats And Bag Store Lockers 5
P03 | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Appreciate the trust has specifically removed these. Please indicate on each locker drawing the location of the lockers and quantity of lockers that could be provided in that area if later required, with the overall number of lockers also listed for reference.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-02-D-O-4001 Staff Workroom Teaching Staff 1 And Teaching Resources Store It Gt Off Corridor 3
P05 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Floating shelving units in the middle of the room away from wall, can a better solution be found.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-02-D-O-4014 Office With Meeting Area, 2 Person 3
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Add desk spacing dims.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-02-D-O-5004 Science Prep Option 1
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Iso & elevations do not match plan.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-02-D-O-5005 Chemical Store 1
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-02-D-O-5020 Science Prep
P03 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Is the fume cupboard located in the best location, limited circulation.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-02-D-O-5102 General Storeroom Central Stock 1
P02 | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31
FS1018-PIN-ZZ-02-D-O-5115 Cleaners' Store 2
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Door opening does not reflect GA plans, which is correct?
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-02-D-O-6113 Coats And Bags Store Lockers 5
P02 | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Appreciate the trust has specifically removed these. Please indicate on each locker drawing the location of the lockers and quantity of lockers that could be provided in that area if later required, with the overall number of lockers also listed for reference.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-02-D-O-7113 Coats And Bags Store Lockers 5
P02 | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Appreciate the trust has specifically removed these. Please indicate on each locker drawing the location of the lockers and quantity of lockers that could be provided in that area if later required, with the overall number of lockers also listed for reference.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-02-D-O-8113 Coats And Bags Store Lockers 5
P02 | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Appreciate the trust has specifically removed these. Please indicate on each locker drawing the location of the lockers and quantity of lockers that could be provided in that area if later required, with the overall number of lockers also listed for reference.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-02-D-O-9113 Coats And Bags Store Lockers 5
P02 | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Appreciate the trust has specifically removed these. Please indicate on each locker drawing the location of the lockers and quantity of lockers that could be provided in that area if later required, with the overall number of lockers also listed for reference.
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-ZZ-L-O-0005 FFE Gap Analysis and Occupancy Schedule
P02 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | To be updated based on review comments
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-ZZ-L-O-0006 Catering Equipment Schedule
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | To be updated based on review comments
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-ZZ-L-O-0007 FFE Cost Plan
P01 | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | To be updated based on review comments
| 2025-03-31 | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-ZZ-M-O-0001 FFE Revit Model
P11 | 2025-04-17 | DFE Review | C - Rejected | 2025-04-17 | Model Number is incorrect in the Splash sheet. Level 01is not displaying in model
|  | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-ZZ-M-O-0002 FFE IFC Model
P09 | 2025-04-09 | DFE Review | A - Accepted | 2025-04-16
| 2025-04-17 | DFE Review | C - Rejected | 2025-04-17 | Not matching native model only level 00 displaying.
|  | Designer Response | Pending | (blank) | (blank)
FS1018-PIN-ZZ-ZZ-M-O-0003 FFE Navis Model
P07 | 2025-04-09 | DFE Review | A - Accepted | 2025-04-16
| 2025-04-17 | DFE Review | A - Accepted | 2025-04-17
FS1018-PIN-ZZ-ZZ-M-O-0004 Catering IFC Model
P03 | 2025-04-09 | DFE Review | A - Accepted | 2025-04-16
FS1018-PIN-ZZ-ZZ-M-O-0005 Catering Revit Model
P03 | 2025-04-16 | Designer Response | Pending | (blank) | (blank)
| 2025-04-09 | DFE Review | C - Rejected | 2025-04-16 | Drawing number and revision on splash sheet not matching submission
FS1018-PIN-ZZ-ZZ-M-O-0006 CATERING NWC MODEL
P02 | 2025-04-09 | DFE Review | A - Accepted | 2025-04-16

## RawData
Project Name | Date Generated
FS1018 DfE Wisbech Free School | 2025-04-24
Document Number | Title | Revision | Workflow Status | Date In | Step Name | Step Outcome | Date of Comments | Comments | Latest revision? | (Helper) Num + Title | (Helper) Hyperlink
FS1018-ADT-ZZ-00-D-J-0001 | BB93 Acoustic Criteria Ground Floor | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Why is there no acoustic performance for the library partition alongside the corridor. The library door should have a 30dB acoustic rating in line with BB93. | TRUE | FS1018-ADT-ZZ-00-D-J-0001 BB93 Acoustic Criteria Ground Floor | FS1018-ADT-ZZ-00-D-J-0001
FS1018-ADT-ZZ-00-D-J-0001 | BB93 Acoustic Criteria Ground Floor | P02 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-ADT-ZZ-00-D-J-0001 BB93 Acoustic Criteria Ground Floor | FS1018-ADT-ZZ-00-D-J-0001
FS1018-ADT-ZZ-00-D-J-0004 | Acoustic Wall Types Ground Floor | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 |  | TRUE | FS1018-ADT-ZZ-00-D-J-0004 Acoustic Wall Types Ground Floor | FS1018-ADT-ZZ-00-D-J-0004
FS1018-ADT-ZZ-01-D-J-0002 | BB93 Acoustic Criteria First Floor | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 |  | TRUE | FS1018-ADT-ZZ-01-D-J-0002 BB93 Acoustic Criteria First Floor | FS1018-ADT-ZZ-01-D-J-0002
FS1018-ADT-ZZ-01-D-J-0005 | Acoustic Wall Types First Floor | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 |  | TRUE | FS1018-ADT-ZZ-01-D-J-0005 Acoustic Wall Types First Floor | FS1018-ADT-ZZ-01-D-J-0005
FS1018-ADT-ZZ-02-D-J-0003 | BB93 Acoustic Criteria Second Floor | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 |  | TRUE | FS1018-ADT-ZZ-02-D-J-0003 BB93 Acoustic Criteria Second Floor | FS1018-ADT-ZZ-02-D-J-0003
FS1018-ADT-ZZ-02-D-J-0006 | Acoustic Wall Types Second Floor | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 |  | TRUE | FS1018-ADT-ZZ-02-D-J-0006 Acoustic Wall Types Second Floor | FS1018-ADT-ZZ-02-D-J-0006
FS1018-ADT-ZZ-ZZ-T-J-0001 | Acoustic Strategy | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Why is there no acoustic performance for the library partition alongside the corridor. The library door should have a 30dB acoustic rating in line with BB93. | TRUE | FS1018-ADT-ZZ-ZZ-T-J-0001 Acoustic Strategy | FS1018-ADT-ZZ-ZZ-T-J-0001
FS1018-ADT-ZZ-ZZ-T-J-0001 | Acoustic Strategy | P02 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-ADT-ZZ-ZZ-T-J-0001 Acoustic Strategy | FS1018-ADT-ZZ-ZZ-T-J-0001
FS1018-ADT-ZZ-ZZ-T-Y-0002 | Environmental Noise Impact Assessment | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 | No further comments | TRUE | FS1018-ADT-ZZ-ZZ-T-Y-0002 Environmental Noise Impact Assessment | FS1018-ADT-ZZ-ZZ-T-Y-0002
FS1018-AGL-ZZ-00-D-E-6110 | Level 00 Containment Sheet 1 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-00-D-E-6110 Level 00 Containment Sheet 1 | FS1018-AGL-ZZ-00-D-E-6110
FS1018-AGL-ZZ-00-D-E-6111 | Level 00 Containment Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-00-D-E-6111 Level 00 Containment Sheet 2 | FS1018-AGL-ZZ-00-D-E-6111
FS1018-AGL-ZZ-00-D-E-6112 | Level 00 Containment Sheet 3 | P01 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-04-02 | Intake duct location not as shown in FS1018-AGL-ZZ-XX-D-E-9511 | TRUE | FS1018-AGL-ZZ-00-D-E-6112 Level 00 Containment Sheet 3 | FS1018-AGL-ZZ-00-D-E-6112
FS1018-AGL-ZZ-00-D-E-6112 | Level 00 Containment Sheet 3 | P01 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-00-D-E-6112 Level 00 Containment Sheet 3 | FS1018-AGL-ZZ-00-D-E-6112
FS1018-AGL-ZZ-00-D-E-6114 | Building Electrical Switchroom Details | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-00-D-E-6114 Building Electrical Switchroom Details | FS1018-AGL-ZZ-00-D-E-6114
FS1018-AGL-ZZ-00-D-E-6210 | Level 00 Small Power And Data Sheet 1 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-00-D-E-6210 Level 00 Small Power And Data Sheet 1 | FS1018-AGL-ZZ-00-D-E-6210
FS1018-AGL-ZZ-00-D-E-6211 | Level 00 Small Power And Data Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-00-D-E-6211 Level 00 Small Power And Data Sheet 2 | FS1018-AGL-ZZ-00-D-E-6211
FS1018-AGL-ZZ-00-D-E-6212 | Level 00 Small Power And Data Sheet 3 | P01 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-02 | Consider adding a general power outlet in the plantroom for maintenance and cleaning | TRUE | FS1018-AGL-ZZ-00-D-E-6212 Level 00 Small Power And Data Sheet 3 | FS1018-AGL-ZZ-00-D-E-6212
FS1018-AGL-ZZ-00-D-E-6212 | Level 00 Small Power And Data Sheet 3 | P01 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-00-D-E-6212 Level 00 Small Power And Data Sheet 3 | FS1018-AGL-ZZ-00-D-E-6212
FS1018-AGL-ZZ-00-D-E-6213 | Level 00 MSER Sheet 1 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-00-D-E-6213 Level 00 MSER Sheet 1 | FS1018-AGL-ZZ-00-D-E-6213
FS1018-AGL-ZZ-00-D-E-6214 | Level 00 MSER Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-00-D-E-6214 Level 00 MSER Sheet 2 | FS1018-AGL-ZZ-00-D-E-6214
FS1018-AGL-ZZ-00-D-E-6215 | Level 00 MSER Sheet 3 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-00-D-E-6215 Level 00 MSER Sheet 3 | FS1018-AGL-ZZ-00-D-E-6215
FS1018-AGL-ZZ-00-D-E-6310 | Level 00 Lighting Sheet 1 | P01 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-04-02 | General and Emergency Lighting not shown for maintenace stair between gridlines A and B. Consider emergency light outside exit at gridline 3A/A and dishwash room. Additional Exit signage shown in Fire Stratergy Report FS1018-OFR-XX-ZZ-G-K-0001 Appendix B. In locations shown yellow in image below and Ground floor gridlines 3A/A, 5/E, 5/K1, 5/M1, 6A/W, 4A/S, 5/R and 6/R | TRUE | FS1018-AGL-ZZ-00-D-E-6310 Level 00 Lighting Sheet 1 | FS1018-AGL-ZZ-00-D-E-6310
FS1018-AGL-ZZ-00-D-E-6310 | Level 00 Lighting Sheet 1 | P01 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-00-D-E-6310 Level 00 Lighting Sheet 1 | FS1018-AGL-ZZ-00-D-E-6310
FS1018-AGL-ZZ-00-D-E-6311 | Level 00 Lighting Sheet 2 | P01 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-04-02 | 1.Additional Exit signage shown in Fire Strategy Report FS1018-OFR-XX-ZZ-G-K-0001 Appendix B, in locations on Ground floor gridlines 3A/A, 5/E, 5/K1, 5/M1, 6A/W, 4A/S, 5/R and 6/R 2.Confirm if area of 01-1101 ICT Classroom 1 and 01-1102 ICT Classroom 2 is les than 60m (as emergency lighting required if over 60m) | TRUE | FS1018-AGL-ZZ-00-D-E-6311 Level 00 Lighting Sheet 2 | FS1018-AGL-ZZ-00-D-E-6311
FS1018-AGL-ZZ-00-D-E-6311 | Level 00 Lighting Sheet 2 | P01 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-00-D-E-6311 Level 00 Lighting Sheet 2 | FS1018-AGL-ZZ-00-D-E-6311
FS1018-AGL-ZZ-00-D-E-6312 | Level 00 Lighting Sheet 3 | P01 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-04-02 | Additional Exit signage shown in Fire Strategy Report FS1018-OFR-XX-ZZ-G-K-0001 Appendix B, in locations on Ground floor gridlines 3A/A, 5/E, 5/K1, 5/M1, 6A/W, 4A/S, 5/R and 6/R Emergency lighting for Rm 00-4015 OFF12 (as you have to go through this room to get to the inner room STN50) | TRUE | FS1018-AGL-ZZ-00-D-E-6312 Level 00 Lighting Sheet 3 | FS1018-AGL-ZZ-00-D-E-6312
FS1018-AGL-ZZ-00-D-E-6312 | Level 00 Lighting Sheet 3 | P01 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-00-D-E-6312 Level 00 Lighting Sheet 3 | FS1018-AGL-ZZ-00-D-E-6312
FS1018-AGL-ZZ-00-D-E-6810 | Level 00 Fire Alarm Sheet 1 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-00-D-E-6810 Level 00 Fire Alarm Sheet 1 | FS1018-AGL-ZZ-00-D-E-6810
FS1018-AGL-ZZ-00-D-E-6811 | Level 00 Fire Alarm Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-00-D-E-6811 Level 00 Fire Alarm Sheet 2 | FS1018-AGL-ZZ-00-D-E-6811
FS1018-AGL-ZZ-00-D-E-6812 | Level 00 Fire Alarm Sheet 3 | P01 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-02 | Contractor to confirm that a fire detection devise is located within 1.5 m from the lift shaft opening On activation of the first silent alarm how is the staff member informed in order to investigate and has this been confirmed with the fire engineer. Interfaces 'GS' is not included in the acronyms | TRUE | FS1018-AGL-ZZ-00-D-E-6812 Level 00 Fire Alarm Sheet 3 | FS1018-AGL-ZZ-00-D-E-6812
FS1018-AGL-ZZ-00-D-E-6812 | Level 00 Fire Alarm Sheet 3 | P01 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-00-D-E-6812 Level 00 Fire Alarm Sheet 3 | FS1018-AGL-ZZ-00-D-E-6812
FS1018-AGL-ZZ-00-D-E-6820 | Level 00 Fire Alarm Zoning Sheet 1 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-00-D-E-6820 Level 00 Fire Alarm Zoning Sheet 1 | FS1018-AGL-ZZ-00-D-E-6820
FS1018-AGL-ZZ-00-D-E-6821 | Level 00 Fire Alarm Zoning Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-00-D-E-6821 Level 00 Fire Alarm Zoning Sheet 2 | FS1018-AGL-ZZ-00-D-E-6821
FS1018-AGL-ZZ-00-D-E-6822 | Level 00 Fire Alarm Zoning Sheet 3 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-00-D-E-6822 Level 00 Fire Alarm Zoning Sheet 3 | FS1018-AGL-ZZ-00-D-E-6822
FS1018-AGL-ZZ-00-D-E-6840 | Level 00 Security Sheet 1 | P01 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-02 | Please confirm that the security, access control and CCTV are to be designed and commissioned by the specialist and the details on the drawing have been reviewed and agreed with the school head of security officer. External CCTV cameras to be IP rated | TRUE | FS1018-AGL-ZZ-00-D-E-6840 Level 00 Security Sheet 1 | FS1018-AGL-ZZ-00-D-E-6840
FS1018-AGL-ZZ-00-D-E-6840 | Level 00 Security Sheet 1 | P01 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-00-D-E-6840 Level 00 Security Sheet 1 | FS1018-AGL-ZZ-00-D-E-6840
FS1018-AGL-ZZ-00-D-E-6841 | Level 00 Security Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-00-D-E-6841 Level 00 Security Sheet 2 | FS1018-AGL-ZZ-00-D-E-6841
FS1018-AGL-ZZ-00-D-E-6842 | Level 00 Security Sheet 3 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-00-D-E-6842 Level 00 Security Sheet 3 | FS1018-AGL-ZZ-00-D-E-6842
FS1018-AGL-ZZ-00-D-E-9001 | Photovoltaic Canopies | P01 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-04-01 | Details need to be updated with confirmed canopy sizes and direct reference to document containing full specification. | TRUE | FS1018-AGL-ZZ-00-D-E-9001 Photovoltaic Canopies | FS1018-AGL-ZZ-00-D-E-9001
FS1018-AGL-ZZ-00-D-E-9001 | Photovoltaic Canopies | P01 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-00-D-E-9001 Photovoltaic Canopies | FS1018-AGL-ZZ-00-D-E-9001
FS1018-AGL-ZZ-00-D-M-5210 | Level 00 Above Ground Drainage Sheet 1 | P02 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | 1. Consider relocating gully out of Cold Room, hygiene perspective 2. Main kitchen, no drains for combi ovens indicated on the drawing; Are we waiting for final kitchen layouts? 3. Numerous areas where pipework clashes with furniture; How is this to be resolved? 4. No high level pipe falls referenced | TRUE | FS1018-AGL-ZZ-00-D-M-5210 Level 00 Above Ground Drainage Sheet 1 | FS1018-AGL-ZZ-00-D-M-5210
FS1018-AGL-ZZ-00-D-M-5210 | Level 00 Above Ground Drainage Sheet 1 | P02 | In Progress | 2025-04-07 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-00-D-M-5210 Level 00 Above Ground Drainage Sheet 1 | FS1018-AGL-ZZ-00-D-M-5210
FS1018-AGL-ZZ-00-D-M-5211 | Level 00 Above Ground Drainage Sheet 2 | P02 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | 1. Changing rooms indicate floor gully's, is this correct? No shower channels? 2. Numerous areas where pipework clashes with furniture; How is this to be resolved? 3. No high level pipe falls referenced 4. Can Condensate drains from HR007 / 008 & HR009 / 010 join together and connect to one Hepvo waterless trap? | TRUE | FS1018-AGL-ZZ-00-D-M-5211 Level 00 Above Ground Drainage Sheet 2 | FS1018-AGL-ZZ-00-D-M-5211
FS1018-AGL-ZZ-00-D-M-5211 | Level 00 Above Ground Drainage Sheet 2 | P02 | In Progress | 2025-04-07 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-00-D-M-5211 Level 00 Above Ground Drainage Sheet 2 | FS1018-AGL-ZZ-00-D-M-5211
FS1018-AGL-ZZ-00-D-M-5212 | Level 00 Above Ground Drainage Sheet 3 | P02 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | WHB waste branch run too long, consider connection into WC float | TRUE | FS1018-AGL-ZZ-00-D-M-5212 Level 00 Above Ground Drainage Sheet 3 | FS1018-AGL-ZZ-00-D-M-5212
FS1018-AGL-ZZ-00-D-M-5212 | Level 00 Above Ground Drainage Sheet 3 | P02 | In Progress | 2025-04-07 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-00-D-M-5212 Level 00 Above Ground Drainage Sheet 3 | FS1018-AGL-ZZ-00-D-M-5212
FS1018-AGL-ZZ-00-D-M-5310 | Level 00 Domestic Water Services Sheet 1 | P02 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | Minor comment - Food Rm - are services to drop within wall or on the surface (Clash with basin) | TRUE | FS1018-AGL-ZZ-00-D-M-5310 Level 00 Domestic Water Services Sheet 1 | FS1018-AGL-ZZ-00-D-M-5310
FS1018-AGL-ZZ-00-D-M-5310 | Level 00 Domestic Water Services Sheet 1 | P02 | In Progress | 2025-04-07 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-00-D-M-5310 Level 00 Domestic Water Services Sheet 1 | FS1018-AGL-ZZ-00-D-M-5310
FS1018-AGL-ZZ-00-D-M-5311 | Level 00 Domestic Water Services Sheet 2 | P02 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-00-D-M-5311 Level 00 Domestic Water Services Sheet 2 | FS1018-AGL-ZZ-00-D-M-5311
FS1018-AGL-ZZ-00-D-M-5312 | Level 00 Domestic Water Services Sheet 3 | P02 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-00-D-M-5312 Level 00 Domestic Water Services Sheet 3 | FS1018-AGL-ZZ-00-D-M-5312
FS1018-AGL-ZZ-00-D-M-5410 | Level 00 Gas | P02 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-00-D-M-5410 Level 00 Gas | FS1018-AGL-ZZ-00-D-M-5410
FS1018-AGL-ZZ-00-D-M-5610 | Level 00 Heating and Cooling Sheet 1 | P01 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Valving arrangement is hard to read- would suggest numbering the typical details and refer to that, or removing entirely. 2. Plantroom drawing reference missing. 3. Symbol missing from Legend. PICV? 4. Should detail actual valve arrangement for underfloor heating (PICV and strainer missing) | TRUE | FS1018-AGL-ZZ-00-D-M-5610 Level 00 Heating and Cooling Sheet 1 | FS1018-AGL-ZZ-00-D-M-5610
FS1018-AGL-ZZ-00-D-M-5610 | Level 00 Heating and Cooling Sheet 1 | P01 | In Progress | 2025-03-27 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-00-D-M-5610 Level 00 Heating and Cooling Sheet 1 | FS1018-AGL-ZZ-00-D-M-5610
FS1018-AGL-ZZ-00-D-M-5611 | Level 00 Heating and Cooling Sheet 2 | P01 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Symbol missing from Legend. PICV? 2. Should detail actual valve arrangement for underfloor heating (PICV and strainer missing) | TRUE | FS1018-AGL-ZZ-00-D-M-5611 Level 00 Heating and Cooling Sheet 2 | FS1018-AGL-ZZ-00-D-M-5611
FS1018-AGL-ZZ-00-D-M-5611 | Level 00 Heating and Cooling Sheet 2 | P01 | In Progress | 2025-03-27 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-00-D-M-5611 Level 00 Heating and Cooling Sheet 2 | FS1018-AGL-ZZ-00-D-M-5611
FS1018-AGL-ZZ-00-D-M-5612 | Level 00 Heating and Cooling Sheet 3 | P01 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Symbol missing from Legend. PICV? 2. Should detail actual valve arrangement for underfloor heating (PICV and strainer missing) | TRUE | FS1018-AGL-ZZ-00-D-M-5612 Level 00 Heating and Cooling Sheet 3 | FS1018-AGL-ZZ-00-D-M-5612
FS1018-AGL-ZZ-00-D-M-5612 | Level 00 Heating and Cooling Sheet 3 | P01 | In Progress | 2025-03-27 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-00-D-M-5612 Level 00 Heating and Cooling Sheet 3 | FS1018-AGL-ZZ-00-D-M-5612
FS1018-AGL-ZZ-00-D-M-5710 | Level 00 Ventilation Sheet 1 | P02 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Fire damper references are missing. 2. Comment that states 'Doesn't fit in CV' This should have been resolved at Stage 4. 3. Comment that states 'Fire damper requirements to be confirmed' This should be resolved at Stage 4. 4. Instances of intake and exhaust louvres being too close together. 5. Comment that states 'Coordination with ceiling to be resolved' This should have been resolved at Stage 4. 6. No access panels shown in ductwork for cleaning as per DW144 | TRUE | FS1018-AGL-ZZ-00-D-M-5710 Level 00 Ventilation Sheet 1 | FS1018-AGL-ZZ-00-D-M-5710
FS1018-AGL-ZZ-00-D-M-5710 | Level 00 Ventilation Sheet 1 | P02 | In Progress | 2025-03-27 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-00-D-M-5710 Level 00 Ventilation Sheet 1 | FS1018-AGL-ZZ-00-D-M-5710
FS1018-AGL-ZZ-00-D-M-5711 | Level 00 Ventilation Sheet 2 | P02 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Fire damper references are missing. 2. Comment that states 'Doesn't fit in CV' This should have been resolved at Stage 4. 3. Instances of intake and exhaust louvres being too close together. 4. Review rationalising number of attenuators on extract ducts in changing rooms. 5. Comment that states 'Coordination with ceiling to be resolved' This should have been resolved at Stage 4. 6. No access panels shown in ductwork for cleaning as per DW144. | TRUE | FS1018-AGL-ZZ-00-D-M-5711 Level 00 Ventilation Sheet 2 | FS1018-AGL-ZZ-00-D-M-5711
FS1018-AGL-ZZ-00-D-M-5711 | Level 00 Ventilation Sheet 2 | P02 | In Progress | 2025-03-27 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-00-D-M-5711 Level 00 Ventilation Sheet 2 | FS1018-AGL-ZZ-00-D-M-5711
FS1018-AGL-ZZ-00-D-M-5712 | Level 00 Ventilation Sheet 3 | P02 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Fire damper references are missing. 2. Instances of intake and exhaust louvres being too close together. 3. Comment that states 'louvre doesn't fit' Should be resolved at Stage 4. 4. No access panels shown in ductwork for cleaning as per DW144 | TRUE | FS1018-AGL-ZZ-00-D-M-5712 Level 00 Ventilation Sheet 3 | FS1018-AGL-ZZ-00-D-M-5712
FS1018-AGL-ZZ-00-D-M-5712 | Level 00 Ventilation Sheet 3 | P02 | In Progress | 2025-03-27 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-00-D-M-5712 Level 00 Ventilation Sheet 3 | FS1018-AGL-ZZ-00-D-M-5712
FS1018-AGL-ZZ-00-D-M-5810 | Level 00 Plantroom Sheet 1 | P01 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-03-27 | 1. Has leak detection been fitted on drip tray over MCP | TRUE | FS1018-AGL-ZZ-00-D-M-5810 Level 00 Plantroom Sheet 1 | FS1018-AGL-ZZ-00-D-M-5810
FS1018-AGL-ZZ-00-D-M-5810 | Level 00 Plantroom Sheet 1 | P01 | In Progress | 2025-03-27 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-00-D-M-5810 Level 00 Plantroom Sheet 1 | FS1018-AGL-ZZ-00-D-M-5810
FS1018-AGL-ZZ-00-D-M-5811 | Level 00 Plantroom Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-00-D-M-5811 Level 00 Plantroom Sheet 2 | FS1018-AGL-ZZ-00-D-M-5811
FS1018-AGL-ZZ-00-D-Z-6010 | Level 00 Builderswork Sheet 1 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-00-D-Z-6010 Level 00 Builderswork Sheet 1 | FS1018-AGL-ZZ-00-D-Z-6010
FS1018-AGL-ZZ-00-D-Z-6011 | Level 00 Builderswork Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-00-D-Z-6011 Level 00 Builderswork Sheet 2 | FS1018-AGL-ZZ-00-D-Z-6011
FS1018-AGL-ZZ-00-D-Z-6012 | Level 00 Builderswork Sheet 3 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-00-D-Z-6012 Level 00 Builderswork Sheet 3 | FS1018-AGL-ZZ-00-D-Z-6012
FS1018-AGL-ZZ-00-D-Z-9610 | Level 00 Reflected Ceiling Plan Sheet 1 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-00-D-Z-9610 Level 00 Reflected Ceiling Plan Sheet 1 | FS1018-AGL-ZZ-00-D-Z-9610
FS1018-AGL-ZZ-00-D-Z-9611 | Level 00 Reflected Ceiling Plan Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-00-D-Z-9611 Level 00 Reflected Ceiling Plan Sheet 2 | FS1018-AGL-ZZ-00-D-Z-9611
FS1018-AGL-ZZ-00-D-Z-9612 | Level 00 Reflected Ceiling Plan Sheet 3 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-00-D-Z-9612 Level 00 Reflected Ceiling Plan Sheet 3 | FS1018-AGL-ZZ-00-D-Z-9612
FS1018-AGL-ZZ-01-D-E-6110 | Level 01 Containment Sheet 1 | P01 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-02 | Containment has a number of branches in each classroom that are not similar to other classroom containment layouts | TRUE | FS1018-AGL-ZZ-01-D-E-6110 Level 01 Containment Sheet 1 | FS1018-AGL-ZZ-01-D-E-6110
FS1018-AGL-ZZ-01-D-E-6110 | Level 01 Containment Sheet 1 | P01 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-01-D-E-6110 Level 01 Containment Sheet 1 | FS1018-AGL-ZZ-01-D-E-6110
FS1018-AGL-ZZ-01-D-E-6111 | Level 01 Containment Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-01-D-E-6111 Level 01 Containment Sheet 2 | FS1018-AGL-ZZ-01-D-E-6111
FS1018-AGL-ZZ-01-D-E-6210 | Level 01 Small Power And Data Sheet 1 | P01 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-02 | Is the amount of small power in the classrooms for the strudents confirmed as acceptable, there seems to be a lot of cable tray compared to other layouts. | TRUE | FS1018-AGL-ZZ-01-D-E-6210 Level 01 Small Power And Data Sheet 1 | FS1018-AGL-ZZ-01-D-E-6210
FS1018-AGL-ZZ-01-D-E-6210 | Level 01 Small Power And Data Sheet 1 | P01 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-01-D-E-6210 Level 01 Small Power And Data Sheet 1 | FS1018-AGL-ZZ-01-D-E-6210
FS1018-AGL-ZZ-01-D-E-6211 | Level 01 Small Power And Data Sheet 2 | P01 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-02 | "The 3No Comms racks have a mix of 16A and 32A supplies, please confirm this is correct. Is the amount of small power in the classrooms confirmed as acceptable, there seems to be a" | TRUE | FS1018-AGL-ZZ-01-D-E-6211 Level 01 Small Power And Data Sheet 2 | FS1018-AGL-ZZ-01-D-E-6211
FS1018-AGL-ZZ-01-D-E-6211 | Level 01 Small Power And Data Sheet 2 | P01 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-01-D-E-6211 Level 01 Small Power And Data Sheet 2 | FS1018-AGL-ZZ-01-D-E-6211
FS1018-AGL-ZZ-01-D-E-6212 | Level 01 MSER Sheet 1 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-01-D-E-6212 Level 01 MSER Sheet 1 | FS1018-AGL-ZZ-01-D-E-6212
FS1018-AGL-ZZ-01-D-E-6213 | Level 01 MSER Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-01-D-E-6213 Level 01 MSER Sheet 2 | FS1018-AGL-ZZ-01-D-E-6213
FS1018-AGL-ZZ-01-D-E-6310 | Level 01 Lighting Sheet 1 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-01-D-E-6310 Level 01 Lighting Sheet 1 | FS1018-AGL-ZZ-01-D-E-6310
FS1018-AGL-ZZ-01-D-E-6311 | Level 01 Lighting Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-01-D-E-6311 Level 01 Lighting Sheet 2 | FS1018-AGL-ZZ-01-D-E-6311
FS1018-AGL-ZZ-01-D-E-6810 | Level 01 Fire Alarm Sheet 1 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-01-D-E-6810 Level 01 Fire Alarm Sheet 1 | FS1018-AGL-ZZ-01-D-E-6810
FS1018-AGL-ZZ-01-D-E-6811 | Level 01 Fire Alarm Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-01-D-E-6811 Level 01 Fire Alarm Sheet 2 | FS1018-AGL-ZZ-01-D-E-6811
FS1018-AGL-ZZ-01-D-E-6820 | Level 01 Fire Alarm Zoning Sheet 1 | P01 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-04-02 | Confirm if stairs will be these own zone as Ground level. | TRUE | FS1018-AGL-ZZ-01-D-E-6820 Level 01 Fire Alarm Zoning Sheet 1 | FS1018-AGL-ZZ-01-D-E-6820
FS1018-AGL-ZZ-01-D-E-6820 | Level 01 Fire Alarm Zoning Sheet 1 | P01 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-01-D-E-6820 Level 01 Fire Alarm Zoning Sheet 1 | FS1018-AGL-ZZ-01-D-E-6820
FS1018-AGL-ZZ-01-D-E-6821 | Level 01 Fire Alarm Zoning Sheet 2 | P01 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-04-02 | Confirm if stairs will be these own zone as Ground level. | TRUE | FS1018-AGL-ZZ-01-D-E-6821 Level 01 Fire Alarm Zoning Sheet 2 | FS1018-AGL-ZZ-01-D-E-6821
FS1018-AGL-ZZ-01-D-E-6821 | Level 01 Fire Alarm Zoning Sheet 2 | P01 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-01-D-E-6821 Level 01 Fire Alarm Zoning Sheet 2 | FS1018-AGL-ZZ-01-D-E-6821
FS1018-AGL-ZZ-01-D-E-6840 | Level 01 Security Sheet 1 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-01-D-E-6840 Level 01 Security Sheet 1 | FS1018-AGL-ZZ-01-D-E-6840
FS1018-AGL-ZZ-01-D-E-6841 | Level 01 Security Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-01-D-E-6841 Level 01 Security Sheet 2 | FS1018-AGL-ZZ-01-D-E-6841
FS1018-AGL-ZZ-01-D-M-5210 | Level 01 Above Ground Drainage Sheet 1 | P02 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | 1. Numerous areas where pipework clashes with furniture; How is this to be resolved? 2. No high level pipe falls referenced 3. Waste traps from cleaners sinks are quite low, please confirm that it is able to connect into the common waste float | TRUE | FS1018-AGL-ZZ-01-D-M-5210 Level 01 Above Ground Drainage Sheet 1 | FS1018-AGL-ZZ-01-D-M-5210
FS1018-AGL-ZZ-01-D-M-5210 | Level 01 Above Ground Drainage Sheet 1 | P02 | In Progress | 2025-04-07 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-01-D-M-5210 Level 01 Above Ground Drainage Sheet 1 | FS1018-AGL-ZZ-01-D-M-5210
FS1018-AGL-ZZ-01-D-M-5211 | Level 01 Above Ground Drainage Sheet 2 | P02 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | 1. Numerous areas where pipework clashes with furniture; How is this to be resolved? 2. No high level pipe falls referenced | TRUE | FS1018-AGL-ZZ-01-D-M-5211 Level 01 Above Ground Drainage Sheet 2 | FS1018-AGL-ZZ-01-D-M-5211
FS1018-AGL-ZZ-01-D-M-5211 | Level 01 Above Ground Drainage Sheet 2 | P02 | In Progress | 2025-04-07 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-01-D-M-5211 Level 01 Above Ground Drainage Sheet 2 | FS1018-AGL-ZZ-01-D-M-5211
FS1018-AGL-ZZ-01-D-M-5310 | Level 01 Domestic Water Services Sheet 1 | P02 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-01-D-M-5310 Level 01 Domestic Water Services Sheet 1 | FS1018-AGL-ZZ-01-D-M-5310
FS1018-AGL-ZZ-01-D-M-5311 | Level 01 Domestic Water Services Sheet 2 | P02 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-01-D-M-5311 Level 01 Domestic Water Services Sheet 2 | FS1018-AGL-ZZ-01-D-M-5311
FS1018-AGL-ZZ-01-D-M-5410 | Level 01 Gas | P02 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | 1. Rising 50 gas pipe in rm 01-1108 Art Rm clashing with furniture 01-6060c, this should be boxed in 2. Gas pipe passing through service riser 01-6060c, should this be pipe-in-pipe? | TRUE | FS1018-AGL-ZZ-01-D-M-5410 Level 01 Gas | FS1018-AGL-ZZ-01-D-M-5410
FS1018-AGL-ZZ-01-D-M-5410 | Level 01 Gas | P02 | In Progress | 2025-04-07 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-01-D-M-5410 Level 01 Gas | FS1018-AGL-ZZ-01-D-M-5410
FS1018-AGL-ZZ-01-D-M-5610 | Level 01 Heating and Cooling Sheet 1 | P01 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Valving arrangement is hard to read- would suggest numbering the typical details and refer to that, or removing entirely. 2. Symbol missing from Legend. PICV? | TRUE | FS1018-AGL-ZZ-01-D-M-5610 Level 01 Heating and Cooling Sheet 1 | FS1018-AGL-ZZ-01-D-M-5610
FS1018-AGL-ZZ-01-D-M-5610 | Level 01 Heating and Cooling Sheet 1 | P01 | In Progress | 2025-03-27 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-01-D-M-5610 Level 01 Heating and Cooling Sheet 1 | FS1018-AGL-ZZ-01-D-M-5610
FS1018-AGL-ZZ-01-D-M-5611 | Level 01 Heating and Cooling Sheet 2 | P01 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Valving arrangement is hard to read- would suggest numbering the typical details and refer to that, or removing entirely. 2. Symbol missing from Legend. PICV? | TRUE | FS1018-AGL-ZZ-01-D-M-5611 Level 01 Heating and Cooling Sheet 2 | FS1018-AGL-ZZ-01-D-M-5611
FS1018-AGL-ZZ-01-D-M-5611 | Level 01 Heating and Cooling Sheet 2 | P01 | In Progress | 2025-03-27 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-01-D-M-5611 Level 01 Heating and Cooling Sheet 2 | FS1018-AGL-ZZ-01-D-M-5611
FS1018-AGL-ZZ-01-D-M-5710 | Level 01 Ventilation Sheet 1 | P02 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Comment that states 'Coordination with ceiling to be resolved' This should have been resolved at Stage 4. 2. GA clashes with legend- needs to be moved. 3. Confirm requirement of fire damper. 4. No access panels shown in ductwork for cleaning as per DW144. | TRUE | FS1018-AGL-ZZ-01-D-M-5710 Level 01 Ventilation Sheet 1 | FS1018-AGL-ZZ-01-D-M-5710
FS1018-AGL-ZZ-01-D-M-5710 | Level 01 Ventilation Sheet 1 | P02 | In Progress | 2025-03-27 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-01-D-M-5710 Level 01 Ventilation Sheet 1 | FS1018-AGL-ZZ-01-D-M-5710
FS1018-AGL-ZZ-01-D-M-5711 | Level 01 Ventilation Sheet 2 | P02 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Comment that states 'Coordination with ceiling to be resolved' This should have been resolved at Stage 4. 2. Louvres are too close together. 3. Confirm no requirement for fire dampers. 4. No access panels shown in ductwork for cleaning as per DW144 | TRUE | FS1018-AGL-ZZ-01-D-M-5711 Level 01 Ventilation Sheet 2 | FS1018-AGL-ZZ-01-D-M-5711
FS1018-AGL-ZZ-01-D-M-5711 | Level 01 Ventilation Sheet 2 | P02 | In Progress | 2025-03-27 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-01-D-M-5711 Level 01 Ventilation Sheet 2 | FS1018-AGL-ZZ-01-D-M-5711
FS1018-AGL-ZZ-01-D-Z-6010 | Level 01 Builderswork Sheet 1 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-01-D-Z-6010 Level 01 Builderswork Sheet 1 | FS1018-AGL-ZZ-01-D-Z-6010
FS1018-AGL-ZZ-01-D-Z-6011 | Level 01 Builderswork Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-01-D-Z-6011 Level 01 Builderswork Sheet 2 | FS1018-AGL-ZZ-01-D-Z-6011
FS1018-AGL-ZZ-01-D-Z-9610 | Level 01 Reflected Ceiling Plan Sheet 1 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-01-D-Z-9610 Level 01 Reflected Ceiling Plan Sheet 1 | FS1018-AGL-ZZ-01-D-Z-9610
FS1018-AGL-ZZ-01-D-Z-9611 | Level 01 Reflected Ceiling Plan Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-01-D-Z-9611 Level 01 Reflected Ceiling Plan Sheet 2 | FS1018-AGL-ZZ-01-D-Z-9611
FS1018-AGL-ZZ-02-D-E-6110 | Level 02 Containment Sheet 1 | P01 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-04-02 | PV Submain route goes through the protected stair, is there an alternative or is this agreed? | TRUE | FS1018-AGL-ZZ-02-D-E-6110 Level 02 Containment Sheet 1 | FS1018-AGL-ZZ-02-D-E-6110
FS1018-AGL-ZZ-02-D-E-6110 | Level 02 Containment Sheet 1 | P01 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-02-D-E-6110 Level 02 Containment Sheet 1 | FS1018-AGL-ZZ-02-D-E-6110
FS1018-AGL-ZZ-02-D-E-6111 | Level 02 Containment Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-02-D-E-6111 Level 02 Containment Sheet 2 | FS1018-AGL-ZZ-02-D-E-6111
FS1018-AGL-ZZ-02-D-E-6210 | Level 02 Small Power And Data Sheet 1 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-02-D-E-6210 Level 02 Small Power And Data Sheet 1 | FS1018-AGL-ZZ-02-D-E-6210
FS1018-AGL-ZZ-02-D-E-6211 | Level 02 Small Power And Data Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-02-D-E-6211 Level 02 Small Power And Data Sheet 2 | FS1018-AGL-ZZ-02-D-E-6211
FS1018-AGL-ZZ-02-D-E-6212 | Level 02 MSER Sheet 1 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-02-D-E-6212 Level 02 MSER Sheet 1 | FS1018-AGL-ZZ-02-D-E-6212
FS1018-AGL-ZZ-02-D-E-6213 | Level 02 MSER Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-02-D-E-6213 Level 02 MSER Sheet 2 | FS1018-AGL-ZZ-02-D-E-6213
FS1018-AGL-ZZ-02-D-E-6310 | Level 02 Lighting Sheet 1 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-02-D-E-6310 Level 02 Lighting Sheet 1 | FS1018-AGL-ZZ-02-D-E-6310
FS1018-AGL-ZZ-02-D-E-6311 | Level 02 Lighting Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-02-D-E-6311 Level 02 Lighting Sheet 2 | FS1018-AGL-ZZ-02-D-E-6311
FS1018-AGL-ZZ-02-D-E-6810 | Level 02 Fire Alarm Sheet 1 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-02-D-E-6810 Level 02 Fire Alarm Sheet 1 | FS1018-AGL-ZZ-02-D-E-6810
FS1018-AGL-ZZ-02-D-E-6811 | Level 02 Fire Alarm Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-02-D-E-6811 Level 02 Fire Alarm Sheet 2 | FS1018-AGL-ZZ-02-D-E-6811
FS1018-AGL-ZZ-02-D-E-6820 | Level 02 Fire Alarm Zoning Sheet 1 | P01 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-04-02 | Confirm if stairs will be these own zone as Ground level. | TRUE | FS1018-AGL-ZZ-02-D-E-6820 Level 02 Fire Alarm Zoning Sheet 1 | FS1018-AGL-ZZ-02-D-E-6820
FS1018-AGL-ZZ-02-D-E-6820 | Level 02 Fire Alarm Zoning Sheet 1 | P01 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-02-D-E-6820 Level 02 Fire Alarm Zoning Sheet 1 | FS1018-AGL-ZZ-02-D-E-6820
FS1018-AGL-ZZ-02-D-E-6821 | Level 02 Fire Alarm Zoning Sheet 2 | P01 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-04-02 | Confirm if stairs will be these own zone as Ground level. | TRUE | FS1018-AGL-ZZ-02-D-E-6821 Level 02 Fire Alarm Zoning Sheet 2 | FS1018-AGL-ZZ-02-D-E-6821
FS1018-AGL-ZZ-02-D-E-6821 | Level 02 Fire Alarm Zoning Sheet 2 | P01 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-02-D-E-6821 Level 02 Fire Alarm Zoning Sheet 2 | FS1018-AGL-ZZ-02-D-E-6821
FS1018-AGL-ZZ-02-D-E-6840 | Level 02 Security Sheet 1 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-02-D-E-6840 Level 02 Security Sheet 1 | FS1018-AGL-ZZ-02-D-E-6840
FS1018-AGL-ZZ-02-D-E-6841 | Level 02 Security Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-02-D-E-6841 Level 02 Security Sheet 2 | FS1018-AGL-ZZ-02-D-E-6841
FS1018-AGL-ZZ-02-D-M-5210 | Level 02 Above Ground Drainage Sheet 1 | P02 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | 1. Numerous areas where pipework clashes with furniture; How is this to be resolved? 2. Science lab sinks - dilution traps or pots? | TRUE | FS1018-AGL-ZZ-02-D-M-5210 Level 02 Above Ground Drainage Sheet 1 | FS1018-AGL-ZZ-02-D-M-5210
FS1018-AGL-ZZ-02-D-M-5210 | Level 02 Above Ground Drainage Sheet 1 | P02 | In Progress | 2025-04-07 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-02-D-M-5210 Level 02 Above Ground Drainage Sheet 1 | FS1018-AGL-ZZ-02-D-M-5210
FS1018-AGL-ZZ-02-D-M-5211 | Level 02 Above Ground Drainage Sheet 2 | P02 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | 1. Pipework clashes with furniture; How is this to be resolved? 2. Waste traps from cleaners sinks are quite low, please confirm that it is able to connect into the common waste float | TRUE | FS1018-AGL-ZZ-02-D-M-5211 Level 02 Above Ground Drainage Sheet 2 | FS1018-AGL-ZZ-02-D-M-5211
FS1018-AGL-ZZ-02-D-M-5211 | Level 02 Above Ground Drainage Sheet 2 | P02 | In Progress | 2025-04-07 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-02-D-M-5211 Level 02 Above Ground Drainage Sheet 2 | FS1018-AGL-ZZ-02-D-M-5211
FS1018-AGL-ZZ-02-D-M-5310 | Level 02 Domestic Water Services Sheet 1 | P02 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-02-D-M-5310 Level 02 Domestic Water Services Sheet 1 | FS1018-AGL-ZZ-02-D-M-5310
FS1018-AGL-ZZ-02-D-M-5311 | Level 02 Domestic Water Services Sheet 2 | P02 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-02-D-M-5311 Level 02 Domestic Water Services Sheet 2 | FS1018-AGL-ZZ-02-D-M-5311
FS1018-AGL-ZZ-02-D-M-5410 | Level 02 Gas | P02 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | CO2 sensors are not indicated in rooms | TRUE | FS1018-AGL-ZZ-02-D-M-5410 Level 02 Gas | FS1018-AGL-ZZ-02-D-M-5410
FS1018-AGL-ZZ-02-D-M-5410 | Level 02 Gas | P02 | In Progress | 2025-04-07 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-02-D-M-5410 Level 02 Gas | FS1018-AGL-ZZ-02-D-M-5410
FS1018-AGL-ZZ-02-D-M-5610 | Level 02 Heating and Cooling Sheet 1 | P01 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Valving arrangement is hard to read- would suggest numbering the typical details and refer to that, or removing entirely. 2. Symbol missing from Legend. PICV? | TRUE | FS1018-AGL-ZZ-02-D-M-5610 Level 02 Heating and Cooling Sheet 1 | FS1018-AGL-ZZ-02-D-M-5610
FS1018-AGL-ZZ-02-D-M-5610 | Level 02 Heating and Cooling Sheet 1 | P01 | In Progress | 2025-03-27 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-02-D-M-5610 Level 02 Heating and Cooling Sheet 1 | FS1018-AGL-ZZ-02-D-M-5610
FS1018-AGL-ZZ-02-D-M-5611 | Level 02 Heating and Cooling Sheet 2 | P01 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Valving arrangement is hard to read- would suggest numbering the typical details and refer to that, or removing entirely. 2. Symbol missing from Legend. PICV? | TRUE | FS1018-AGL-ZZ-02-D-M-5611 Level 02 Heating and Cooling Sheet 2 | FS1018-AGL-ZZ-02-D-M-5611
FS1018-AGL-ZZ-02-D-M-5611 | Level 02 Heating and Cooling Sheet 2 | P01 | In Progress | 2025-03-27 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-02-D-M-5611 Level 02 Heating and Cooling Sheet 2 | FS1018-AGL-ZZ-02-D-M-5611
FS1018-AGL-ZZ-02-D-M-5710 | Level 02 Ventilation Sheet 1 | P02 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-02-D-M-5710 Level 02 Ventilation Sheet 1 | FS1018-AGL-ZZ-02-D-M-5710
FS1018-AGL-ZZ-02-D-M-5711 | Level 02 Ventilation Sheet 2 | P02 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Comment that states 'Coordination with ceiling to be resolved' This should have been resolved at Stage 4. 2. Confirm requirement of fire damper. 3. No access panels shown in ductwork for cleaning as per DW144. | TRUE | FS1018-AGL-ZZ-02-D-M-5711 Level 02 Ventilation Sheet 2 | FS1018-AGL-ZZ-02-D-M-5711
FS1018-AGL-ZZ-02-D-M-5711 | Level 02 Ventilation Sheet 2 | P02 | In Progress | 2025-03-27 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-02-D-M-5711 Level 02 Ventilation Sheet 2 | FS1018-AGL-ZZ-02-D-M-5711
FS1018-AGL-ZZ-02-D-Z-6010 | Level 02 Builderswork Sheet 1 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-02-D-Z-6010 Level 02 Builderswork Sheet 1 | FS1018-AGL-ZZ-02-D-Z-6010
FS1018-AGL-ZZ-02-D-Z-6011 | Level 02 Builderswork Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-02-D-Z-6011 Level 02 Builderswork Sheet 2 | FS1018-AGL-ZZ-02-D-Z-6011
FS1018-AGL-ZZ-02-D-Z-9610 | Level 02 Reflected Ceiling Plan Sheet 1 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-02-D-Z-9610 Level 02 Reflected Ceiling Plan Sheet 1 | FS1018-AGL-ZZ-02-D-Z-9610
FS1018-AGL-ZZ-02-D-Z-9611 | Level 02 Reflected Ceiling Plan Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-02-D-Z-9611 Level 02 Reflected Ceiling Plan Sheet 2 | FS1018-AGL-ZZ-02-D-Z-9611
FS1018-AGL-ZZ-RF-D-E-6213 | Roof Level MSER | P01 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-04-02 | "Cable contanment to Power supplies are not shown on a drawing, add note stating form of cable protection. Accronym list needs updating i.e. OD, HTU,LWH,GSV, EF,PSV etc" | TRUE | FS1018-AGL-ZZ-RF-D-E-6213 Roof Level MSER | FS1018-AGL-ZZ-RF-D-E-6213
FS1018-AGL-ZZ-RF-D-E-6213 | Roof Level MSER | P01 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-RF-D-E-6213 Roof Level MSER | FS1018-AGL-ZZ-RF-D-E-6213
FS1018-AGL-ZZ-RF-D-E-6810 | Roof Level Fire Alarm Sheet 1 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-RF-D-E-6810 Roof Level Fire Alarm Sheet 1 | FS1018-AGL-ZZ-RF-D-E-6810
FS1018-AGL-ZZ-RF-D-E-6811 | Roof Level Fire Alarm Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-RF-D-E-6811 Roof Level Fire Alarm Sheet 2 | FS1018-AGL-ZZ-RF-D-E-6811
FS1018-AGL-ZZ-RF-D-E-6840 | Roof Level Security Sheet 1 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-RF-D-E-6840 Roof Level Security Sheet 1 | FS1018-AGL-ZZ-RF-D-E-6840
FS1018-AGL-ZZ-RF-D-E-6841 | Roof Level Security Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-RF-D-E-6841 Roof Level Security Sheet 2 | FS1018-AGL-ZZ-RF-D-E-6841
FS1018-AGL-ZZ-RF-D-E-6842 | Roof Level Security Sheet 3 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-RF-D-E-6842 Roof Level Security Sheet 3 | FS1018-AGL-ZZ-RF-D-E-6842
FS1018-AGL-ZZ-RF-D-E-9001 | Photovoltaic | P02 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-04-01 | Details need to be updated to be consistent with latest design document and associated calculations used in energy modelling. | TRUE | FS1018-AGL-ZZ-RF-D-E-9001 Photovoltaic | FS1018-AGL-ZZ-RF-D-E-9001
FS1018-AGL-ZZ-RF-D-E-9001 | Photovoltaic | P02 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-RF-D-E-9001 Photovoltaic | FS1018-AGL-ZZ-RF-D-E-9001
FS1018-AGL-ZZ-RF-D-M-5210 | Roof Level Above Ground Drainage Sheet 1 | P02 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-RF-D-M-5210 Roof Level Above Ground Drainage Sheet 1 | FS1018-AGL-ZZ-RF-D-M-5210
FS1018-AGL-ZZ-RF-D-M-5211 | Roof Level Above Ground Drainage Sheet 2 | P02 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-RF-D-M-5211 Roof Level Above Ground Drainage Sheet 2 | FS1018-AGL-ZZ-RF-D-M-5211
FS1018-AGL-ZZ-RF-D-M-5212 | Roof Level Above Ground Drainage Sheet 3 | P02 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-RF-D-M-5212 Roof Level Above Ground Drainage Sheet 3 | FS1018-AGL-ZZ-RF-D-M-5212
FS1018-AGL-ZZ-RF-D-M-5310 | Roof Level Domestic Water Services Sheet 1 | P02 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-RF-D-M-5310 Roof Level Domestic Water Services Sheet 1 | FS1018-AGL-ZZ-RF-D-M-5310
FS1018-AGL-ZZ-RF-D-M-5311 | Roof Level Domestic Water Services Sheet 2 | P02 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-RF-D-M-5311 Roof Level Domestic Water Services Sheet 2 | FS1018-AGL-ZZ-RF-D-M-5311
FS1018-AGL-ZZ-RF-D-M-5312 | Roof Level Domestic Water Services Sheet 3 | P02 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-RF-D-M-5312 Roof Level Domestic Water Services Sheet 3 | FS1018-AGL-ZZ-RF-D-M-5312
FS1018-AGL-ZZ-RF-D-M-5710 | Roof Level Ventilation Sheet 1 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-RF-D-M-5710 Roof Level Ventilation Sheet 1 | FS1018-AGL-ZZ-RF-D-M-5710
FS1018-AGL-ZZ-RF-D-M-5711 | Roof Level Ventilation Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-RF-D-M-5711 Roof Level Ventilation Sheet 2 | FS1018-AGL-ZZ-RF-D-M-5711
FS1018-AGL-ZZ-RF-D-M-5712 | Roof Level Ventilation Sheet 3 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-RF-D-M-5712 Roof Level Ventilation Sheet 3 | FS1018-AGL-ZZ-RF-D-M-5712
FS1018-AGL-ZZ-RF-D-Z-5810 | Roof Level Plantroom Sheet 1 | P02 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-RF-D-Z-5810 Roof Level Plantroom Sheet 1 | FS1018-AGL-ZZ-RF-D-Z-5810
FS1018-AGL-ZZ-RF-D-Z-5811 | Roof Level Plantroom Sheet 2 | P02 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-RF-D-Z-5811 Roof Level Plantroom Sheet 2 | FS1018-AGL-ZZ-RF-D-Z-5811
FS1018-AGL-ZZ-RF-D-Z-5812 | Roof Level Plantroom Sheet 3 | P02 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-RF-D-Z-5812 Roof Level Plantroom Sheet 3 | FS1018-AGL-ZZ-RF-D-Z-5812
FS1018-AGL-ZZ-RF-D-Z-6010 | Roof Level Builderswork Sheet 1 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-RF-D-Z-6010 Roof Level Builderswork Sheet 1 | FS1018-AGL-ZZ-RF-D-Z-6010
FS1018-AGL-ZZ-RF-D-Z-6011 | Roof Level Builderswork Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-RF-D-Z-6011 Roof Level Builderswork Sheet 2 | FS1018-AGL-ZZ-RF-D-Z-6011
FS1018-AGL-ZZ-RF-D-Z-6012 | Roof Level Builderswork Sheet 3 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-RF-D-Z-6012 Roof Level Builderswork Sheet 3 | FS1018-AGL-ZZ-RF-D-Z-6012
FS1018-AGL-ZZ-XX-D-E-9001 | External Lighting | P04 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-02 | Contractor to confirm: No lighting under 2No of 3No PV Canopies and School Pitch and Games Court. External Luminaires are not in the luminaire schedule From Stage 3 comments (Item 20) Contractors response was that no external lighting was provided outside those on the final exits, due to there not being designated muster points. Has this been confirmed as acceptable with the Fire Engineer/Building Control. | TRUE | FS1018-AGL-ZZ-XX-D-E-9001 External Lighting | FS1018-AGL-ZZ-XX-D-E-9001
FS1018-AGL-ZZ-XX-D-E-9001 | External Lighting | P04 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-XX-D-E-9001 External Lighting | FS1018-AGL-ZZ-XX-D-E-9001
FS1018-AGL-ZZ-XX-D-E-9002 | External Lighting Lux Levels | P02 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-XX-D-E-9002 External Lighting Lux Levels | FS1018-AGL-ZZ-XX-D-E-9002
FS1018-AGL-ZZ-XX-D-E-9511 | DNO Services Drawing and Proposal | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-XX-D-E-9511 DNO Services Drawing and Proposal | FS1018-AGL-ZZ-XX-D-E-9511
FS1018-AGL-ZZ-XX-D-Z-5810 | External Compound | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-D-Z-5810 External Compound | FS1018-AGL-ZZ-XX-D-Z-5810
FS1018-AGL-ZZ-XX-D-Z-9510 | External Services | P03 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-XX-D-Z-9510 External Services | FS1018-AGL-ZZ-XX-D-Z-9510
FS1018-AGL-ZZ-XX-L-E-0001 | Proposed Manufacturers Electrical Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-XX-L-E-0001 Proposed Manufacturers Electrical Schedule | FS1018-AGL-ZZ-XX-L-E-0001
FS1018-AGL-ZZ-XX-L-E-0002 | Cable Calculation & Schedule Report | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-XX-L-E-0002 Cable Calculation & Schedule Report | FS1018-AGL-ZZ-XX-L-E-0002
FS1018-AGL-ZZ-XX-L-E-0003 | Containment Calculations | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-XX-L-E-0003 Containment Calculations | FS1018-AGL-ZZ-XX-L-E-0003
FS1018-AGL-ZZ-XX-L-E-0004 | Lighting Calculations | P01 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-04-02 | Assemby Hall achieving 300lux rather than 500lux. Servery not achieving 300lux. For Music Room and DT workshop, consider spacing the emergency lighting at edge rather than centre to improve the min emergency lighting level (currently under 0.5lux and 15lux) In Stage 3 comments (Item3) WSP asks for 200lux to lift as SLL code for lighting 200lux, confirm this has been calculated. | TRUE | FS1018-AGL-ZZ-XX-L-E-0004 Lighting Calculations | FS1018-AGL-ZZ-XX-L-E-0004
FS1018-AGL-ZZ-XX-L-E-0004 | Lighting Calculations | P01 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-XX-L-E-0004 Lighting Calculations | FS1018-AGL-ZZ-XX-L-E-0004
FS1018-AGL-ZZ-XX-L-E-0005 | Exit Signage Calculation | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-XX-L-E-0005 Exit Signage Calculation | FS1018-AGL-ZZ-XX-L-E-0005
FS1018-AGL-ZZ-XX-L-E-9602 | Luminaire Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-XX-L-E-9602 Luminaire Schedule | FS1018-AGL-ZZ-XX-L-E-9602
FS1018-AGL-ZZ-XX-L-M-0003 | Domestic Water Services Calculations | P01 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | HWSR no flow rate indicated in calcs | TRUE | FS1018-AGL-ZZ-XX-L-M-0003 Domestic Water Services Calculations | FS1018-AGL-ZZ-XX-L-M-0003
FS1018-AGL-ZZ-XX-L-M-0003 | Domestic Water Services Calculations | P01 | In Progress | 2025-04-07 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-XX-L-M-0003 Domestic Water Services Calculations | FS1018-AGL-ZZ-XX-L-M-0003
FS1018-AGL-ZZ-XX-L-M-0004 | Ventilation Calculations | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-0004 Ventilation Calculations | FS1018-AGL-ZZ-XX-L-M-0004
FS1018-AGL-ZZ-XX-L-M-0005 | Gas Calculations | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-0005 Gas Calculations | FS1018-AGL-ZZ-XX-L-M-0005
FS1018-AGL-ZZ-XX-L-M-0006 | Above Ground Drainage Calculations | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-0006 Above Ground Drainage Calculations | FS1018-AGL-ZZ-XX-L-M-0006
FS1018-AGL-ZZ-XX-L-M-0007 | Heating Calculations | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-0007 Heating Calculations | FS1018-AGL-ZZ-XX-L-M-0007
FS1018-AGL-ZZ-XX-L-M-0008 | Heat Source Calculations | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-0008 Heat Source Calculations | FS1018-AGL-ZZ-XX-L-M-0008
FS1018-AGL-ZZ-XX-L-M-9604 | Heat Pump Schedule | P01 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | Why N+1 for heating and 66% load per ASHP for DHW? (neither are incorrect). Should there be 7 units to provide N+1 according to your calculation? | TRUE | FS1018-AGL-ZZ-XX-L-M-9604 Heat Pump Schedule | FS1018-AGL-ZZ-XX-L-M-9604
FS1018-AGL-ZZ-XX-L-M-9604 | Heat Pump Schedule | P01 | In Progress | 2025-03-27 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9604 Heat Pump Schedule | FS1018-AGL-ZZ-XX-L-M-9604
FS1018-AGL-ZZ-XX-L-M-9605 | Buffer Vessel Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9605 Buffer Vessel Schedule | FS1018-AGL-ZZ-XX-L-M-9605
FS1018-AGL-ZZ-XX-L-M-9607 | Plate Heat Exchanger Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9607 Plate Heat Exchanger Schedule | FS1018-AGL-ZZ-XX-L-M-9607
FS1018-AGL-ZZ-XX-L-M-9608 | Water Heater Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9608 Water Heater Schedule | FS1018-AGL-ZZ-XX-L-M-9608
FS1018-AGL-ZZ-XX-L-M-9609 | Air & Dirt Separator Schedule | P01 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-03-27 | AD01 flowrate does not match schematic | TRUE | FS1018-AGL-ZZ-XX-L-M-9609 Air & Dirt Separator Schedule | FS1018-AGL-ZZ-XX-L-M-9609
FS1018-AGL-ZZ-XX-L-M-9609 | Air & Dirt Separator Schedule | P01 | In Progress | 2025-03-27 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9609 Air & Dirt Separator Schedule | FS1018-AGL-ZZ-XX-L-M-9609
FS1018-AGL-ZZ-XX-L-M-9610 | Dosing Pot Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9610 Dosing Pot Schedule | FS1018-AGL-ZZ-XX-L-M-9610
FS1018-AGL-ZZ-XX-L-M-9613 | Water Filter Schedule | P01 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-03-27 | Flowrate does not match schematic | TRUE | FS1018-AGL-ZZ-XX-L-M-9613 Water Filter Schedule | FS1018-AGL-ZZ-XX-L-M-9613
FS1018-AGL-ZZ-XX-L-M-9613 | Water Filter Schedule | P01 | In Progress | 2025-03-27 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9613 Water Filter Schedule | FS1018-AGL-ZZ-XX-L-M-9613
FS1018-AGL-ZZ-XX-L-M-9614 | Water Softener Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9614 Water Softener Schedule | FS1018-AGL-ZZ-XX-L-M-9614
FS1018-AGL-ZZ-XX-L-M-9617 | Leak Detection Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9617 Leak Detection Schedule | FS1018-AGL-ZZ-XX-L-M-9617
FS1018-AGL-ZZ-XX-L-M-9619 | Gas Meter Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9619 Gas Meter Schedule | FS1018-AGL-ZZ-XX-L-M-9619
FS1018-AGL-ZZ-XX-L-M-9620 | Water Meter Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9620 Water Meter Schedule | FS1018-AGL-ZZ-XX-L-M-9620
FS1018-AGL-ZZ-XX-L-M-9621 | Heat Meter Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9621 Heat Meter Schedule | FS1018-AGL-ZZ-XX-L-M-9621
FS1018-AGL-ZZ-XX-L-M-9623 | Gas Solenoid Valve Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9623 Gas Solenoid Valve Schedule | FS1018-AGL-ZZ-XX-L-M-9623
FS1018-AGL-ZZ-XX-L-M-9624 | Gas Detection & Proving Panel Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9624 Gas Detection & Proving Panel Schedule | FS1018-AGL-ZZ-XX-L-M-9624
FS1018-AGL-ZZ-XX-L-M-9625 | Pressurisation Unit Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9625 Pressurisation Unit Schedule | FS1018-AGL-ZZ-XX-L-M-9625
FS1018-AGL-ZZ-XX-L-M-9627 | Storage Tank Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9627 Storage Tank Schedule | FS1018-AGL-ZZ-XX-L-M-9627
FS1018-AGL-ZZ-XX-L-M-9628 | Booster Set Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9628 Booster Set Schedule | FS1018-AGL-ZZ-XX-L-M-9628
FS1018-AGL-ZZ-XX-L-M-9630 | Pump Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9630 Pump Schedule | FS1018-AGL-ZZ-XX-L-M-9630
FS1018-AGL-ZZ-XX-L-M-9634 | Local Water Heater Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9634 Local Water Heater Schedule | FS1018-AGL-ZZ-XX-L-M-9634
FS1018-AGL-ZZ-XX-L-M-9637 | Radiator Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9637 Radiator Schedule | FS1018-AGL-ZZ-XX-L-M-9637
FS1018-AGL-ZZ-XX-L-M-9641 | Underfloor Heating Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9641 Underfloor Heating Schedule | FS1018-AGL-ZZ-XX-L-M-9641
FS1018-AGL-ZZ-XX-L-M-9642 | Underfloor Heating Manifold Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9642 Underfloor Heating Manifold Schedule | FS1018-AGL-ZZ-XX-L-M-9642
FS1018-AGL-ZZ-XX-L-M-9644 | Overdoor Heater Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9644 Overdoor Heater Schedule | FS1018-AGL-ZZ-XX-L-M-9644
FS1018-AGL-ZZ-XX-L-M-9647 | Electric Heater Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9647 Electric Heater Schedule | FS1018-AGL-ZZ-XX-L-M-9647
FS1018-AGL-ZZ-XX-L-M-9649 | Fan Convector Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9649 Fan Convector Schedule | FS1018-AGL-ZZ-XX-L-M-9649
FS1018-AGL-ZZ-XX-L-M-9652 | Air Handling Unit Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9652 Air Handling Unit Schedule | FS1018-AGL-ZZ-XX-L-M-9652
FS1018-AGL-ZZ-XX-L-M-9653 | Heat Recovery Unit Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9653 Heat Recovery Unit Schedule | FS1018-AGL-ZZ-XX-L-M-9653
FS1018-AGL-ZZ-XX-L-M-9654 | Hybrid Ventilation Unit Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9654 Hybrid Ventilation Unit Schedule | FS1018-AGL-ZZ-XX-L-M-9654
FS1018-AGL-ZZ-XX-L-M-9655 | Fan Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9655 Fan Schedule | FS1018-AGL-ZZ-XX-L-M-9655
FS1018-AGL-ZZ-XX-L-M-9658 | Louvre Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9658 Louvre Schedule | FS1018-AGL-ZZ-XX-L-M-9658
FS1018-AGL-ZZ-XX-L-M-9659 | Supply Diffuser Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9659 Supply Diffuser Schedule | FS1018-AGL-ZZ-XX-L-M-9659
FS1018-AGL-ZZ-XX-L-M-9660 | Extract Grille Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9660 Extract Grille Schedule | FS1018-AGL-ZZ-XX-L-M-9660
FS1018-AGL-ZZ-XX-L-M-9661 | Attenuator Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9661 Attenuator Schedule | FS1018-AGL-ZZ-XX-L-M-9661
FS1018-AGL-ZZ-XX-L-M-9662 | Transfer Grille Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9662 Transfer Grille Schedule | FS1018-AGL-ZZ-XX-L-M-9662
FS1018-AGL-ZZ-XX-L-M-9671 | Heating Coil Schedule (LTHW) | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9671 Heating Coil Schedule (LTHW) | FS1018-AGL-ZZ-XX-L-M-9671
FS1018-AGL-ZZ-XX-L-M-9675 | Smoke-activated Fire Damper Schedule | P01 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | There are dampers missing that are shown on the layout but not on the schedule | TRUE | FS1018-AGL-ZZ-XX-L-M-9675 Smoke-activated Fire Damper Schedule | FS1018-AGL-ZZ-XX-L-M-9675
FS1018-AGL-ZZ-XX-L-M-9675 | Smoke-activated Fire Damper Schedule | P01 | In Progress | 2025-03-27 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9675 Smoke-activated Fire Damper Schedule | FS1018-AGL-ZZ-XX-L-M-9675
FS1018-AGL-ZZ-XX-L-M-9678 | Passive Stack Ventilator Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9678 Passive Stack Ventilator Schedule | FS1018-AGL-ZZ-XX-L-M-9678
FS1018-AGL-ZZ-XX-L-M-9681 | DX Indoor Unit Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9681 DX Indoor Unit Schedule | FS1018-AGL-ZZ-XX-L-M-9681
FS1018-AGL-ZZ-XX-L-M-9682 | DX Outdoor Unit Schedule | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-L-M-9682 DX Outdoor Unit Schedule | FS1018-AGL-ZZ-XX-L-M-9682
FS1018-AGL-ZZ-XX-L-Z-0001 | Designers MEP Risk Assessment | P02 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-XX-L-Z-0001 Designers MEP Risk Assessment | FS1018-AGL-ZZ-XX-L-Z-0001
FS1018-AGL-ZZ-XX-L-Z-0004 | Heat Loss Calculations | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-01 | No further comments | TRUE | FS1018-AGL-ZZ-XX-L-Z-0004 Heat Loss Calculations | FS1018-AGL-ZZ-XX-L-Z-0004
FS1018-AGL-ZZ-XX-T-E-0001 | Electrical Specification | P01 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-02 | "Outstanding stage 3 comment WSP Comment:BS5839-1 says fire alarm sounder should not be used for purposes other than warning of fire, unless the response required is identical to that required in the event of fire (i.e immediate evacuation by use of all escape routes). However, as an established exception, the fire alarm signal may be used in schools to indicate start or finish of predetermined periods. The duration of such signal should not exceed 5s. Please confirm if the PA system and the class change system are independent of the fire alarm system. Responce: 'Discussions took place concerning the requirement of a class change system and the desired complexity involved regarding the PA system but no confirmation has been given. Current initial intention is to use the FA signal to indicate start or finish of classes, what is the schools desired preference?" | TRUE | FS1018-AGL-ZZ-XX-T-E-0001 Electrical Specification | FS1018-AGL-ZZ-XX-T-E-0001
FS1018-AGL-ZZ-XX-T-E-0001 | Electrical Specification | P01 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-XX-T-E-0001 Electrical Specification | FS1018-AGL-ZZ-XX-T-E-0001
FS1018-AGL-ZZ-XX-T-E-0003 | Electrical Maximum Demand | P02 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-02 | "Outstanding Stage 3 comment WSP Comment: Please confirm that the total power requirement for electric vehicle charging corresponds to the number of parking bays available on site. Check SoA for GIFA Responce: Assumed total power requirement for electric vehicle charging was based off 14No. Parking Spots (including disabled) outside the front of the school. WSP Current comment: there are currently 9no in the max demand, is this correct." | TRUE | FS1018-AGL-ZZ-XX-T-E-0003 Electrical Maximum Demand | FS1018-AGL-ZZ-XX-T-E-0003
FS1018-AGL-ZZ-XX-T-E-0003 | Electrical Maximum Demand | P02 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-XX-T-E-0003 Electrical Maximum Demand | FS1018-AGL-ZZ-XX-T-E-0003
FS1018-AGL-ZZ-XX-T-M-0001 | Mechanical Specification | P01 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-04-01 | 1. Page 44. Number of ASHP contradicts schedule. 2. Page 51. Refers to DHW and not heating 3. Confirm ABS or MUPVC for small diameter waste pipes 4. Confirm if ABS or uPVC drainage stacks | TRUE | FS1018-AGL-ZZ-XX-T-M-0001 Mechanical Specification | FS1018-AGL-ZZ-XX-T-M-0001
FS1018-AGL-ZZ-XX-T-M-0001 | Mechanical Specification | P01 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-XX-T-M-0001 Mechanical Specification | FS1018-AGL-ZZ-XX-T-M-0001
FS1018-AGL-ZZ-XX-T-Z-0002 | Plant Access Maintenance And Replacement Strategy | P02 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-04-01 | 1. Document number does not match what is in the report. 2. MVHR- has access/access panels been coordinated with architect? 3. Confirm the access, maintenance, and replacement strategy for lighting and smoke detection systems in the assembly halls and sports hall. | TRUE | FS1018-AGL-ZZ-XX-T-Z-0002 Plant Access Maintenance And Replacement Strategy | FS1018-AGL-ZZ-XX-T-Z-0002
FS1018-AGL-ZZ-XX-T-Z-0002 | Plant Access Maintenance And Replacement Strategy | P02 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-XX-T-Z-0002 Plant Access Maintenance And Replacement Strategy | FS1018-AGL-ZZ-XX-T-Z-0002
FS1018-AGL-ZZ-XX-T-Z-0006 | NBS Project Description | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-XX-T-Z-0006 NBS Project Description | FS1018-AGL-ZZ-XX-T-Z-0006
FS1018-AGL-ZZ-XX-T-Z-0007 | Thermal Modelling, Compliance & Sustainability Report | P01 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-04-01 | Need to ensure consistency with Solar PV modelling and make clear if IES modelled output is used in compliance calculations. Also need to update details to remove reference to Newcastle City Council - and ensure local planning guidance is accurate (as applicable to the current scheme). | TRUE | FS1018-AGL-ZZ-XX-T-Z-0007 Thermal Modelling, Compliance & Sustainability Report | FS1018-AGL-ZZ-XX-T-Z-0007
FS1018-AGL-ZZ-XX-T-Z-0007 | Thermal Modelling, Compliance & Sustainability Report | P01 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-XX-T-Z-0007 Thermal Modelling, Compliance & Sustainability Report | FS1018-AGL-ZZ-XX-T-Z-0007
FS1018-AGL-ZZ-ZZ-D-E-9001 | Lightning Protection | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-ZZ-D-E-9001 Lightning Protection | FS1018-AGL-ZZ-ZZ-D-E-9001
FS1018-AGL-ZZ-ZZ-D-Z-6115 | Server and Hub Room | P01 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-03-27 | 1. Where is the condensate drainage pipework? | TRUE | FS1018-AGL-ZZ-ZZ-D-Z-6115 Server and Hub Room | FS1018-AGL-ZZ-ZZ-D-Z-6115
FS1018-AGL-ZZ-ZZ-D-Z-6115 | Server and Hub Room | P01 | In Progress | 2025-03-27 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-ZZ-D-Z-6115 Server and Hub Room | FS1018-AGL-ZZ-ZZ-D-Z-6115
FS1018-AGL-ZZ-ZZ-D-Z-9610 | Typical D&T Classroom | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-ZZ-D-Z-9610 Typical D&T Classroom | FS1018-AGL-ZZ-ZZ-D-Z-9610
FS1018-AGL-ZZ-ZZ-D-Z-9611 | Typical Food Room | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-ZZ-D-Z-9611 Typical Food Room | FS1018-AGL-ZZ-ZZ-D-Z-9611
FS1018-AGL-ZZ-ZZ-D-Z-9612 | Typical ICT Classroom | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-ZZ-D-Z-9612 Typical ICT Classroom | FS1018-AGL-ZZ-ZZ-D-Z-9612
FS1018-AGL-ZZ-ZZ-D-Z-9613 | Typical Riser | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-ZZ-D-Z-9613 Typical Riser | FS1018-AGL-ZZ-ZZ-D-Z-9613
FS1018-AGL-ZZ-ZZ-D-Z-9614 | Typical Science Room | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-ZZ-D-Z-9614 Typical Science Room | FS1018-AGL-ZZ-ZZ-D-Z-9614
FS1018-AGL-ZZ-ZZ-G-E-6010 | LV Schematic Sheet 1 | P01 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-04-02 | Breaker settings show allot of TBC. Please confirm that breaker to SB-02 (Way 25 on SB-01) discriminates with upstream device. | TRUE | FS1018-AGL-ZZ-ZZ-G-E-6010 LV Schematic Sheet 1 | FS1018-AGL-ZZ-ZZ-G-E-6010
FS1018-AGL-ZZ-ZZ-G-E-6010 | LV Schematic Sheet 1 | P01 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-ZZ-G-E-6010 LV Schematic Sheet 1 | FS1018-AGL-ZZ-ZZ-G-E-6010
FS1018-AGL-ZZ-ZZ-G-E-6011 | LV Schematic Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-ZZ-G-E-6011 LV Schematic Sheet 2 | FS1018-AGL-ZZ-ZZ-G-E-6011
FS1018-AGL-ZZ-ZZ-G-E-6811 | Fire Alarm Schematic | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-02 |  | TRUE | FS1018-AGL-ZZ-ZZ-G-E-6811 Fire Alarm Schematic | FS1018-AGL-ZZ-ZZ-G-E-6811
FS1018-AGL-ZZ-ZZ-G-M-5010 | Controls Schematic | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-01 |  | TRUE | FS1018-AGL-ZZ-ZZ-G-M-5010 Controls Schematic | FS1018-AGL-ZZ-ZZ-G-M-5010
FS1018-AGL-ZZ-ZZ-G-M-5210 | Above Ground Drainage Schematic Sheet 1 | P01 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | 1. Remove stack vent detail 2. Relocate gully in Cold Room, hygiene perspective 3. Review cleaners sink waste connection; Cleaner sinks have low waste connections; Confirm that connection will connect to common waste float 4. There are single stub stacks with no top RE FW19 5. There are no Hepvo waterless traps indicated on the schematic for condensate drains.. 6. Can condensate units HR007/0008 waste join together? 7. Can condensate units HR009/010 waste join together? | TRUE | FS1018-AGL-ZZ-ZZ-G-M-5210 Above Ground Drainage Schematic Sheet 1 | FS1018-AGL-ZZ-ZZ-G-M-5210
FS1018-AGL-ZZ-ZZ-G-M-5210 | Above Ground Drainage Schematic Sheet 1 | P01 | In Progress | 2025-04-07 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-ZZ-G-M-5210 Above Ground Drainage Schematic Sheet 1 | FS1018-AGL-ZZ-ZZ-G-M-5210
FS1018-AGL-ZZ-ZZ-G-M-5211 | Above Ground Drainage Schematic Sheet 2 | P01 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | 1. Remove stack vent detail 2. FG13 and add SH designation 3. Consider WHB 00-6018 & 00-6042a waste pipes connecting into the WC common float; Length of waste run looks too far from stack. | TRUE | FS1018-AGL-ZZ-ZZ-G-M-5211 Above Ground Drainage Schematic Sheet 2 | FS1018-AGL-ZZ-ZZ-G-M-5211
FS1018-AGL-ZZ-ZZ-G-M-5211 | Above Ground Drainage Schematic Sheet 2 | P01 | In Progress | 2025-04-07 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-ZZ-G-M-5211 Above Ground Drainage Schematic Sheet 2 | FS1018-AGL-ZZ-ZZ-G-M-5211
FS1018-AGL-ZZ-ZZ-G-M-5310 | Domestic Water Services Schematic | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-07 |  | TRUE | FS1018-AGL-ZZ-ZZ-G-M-5310 Domestic Water Services Schematic | FS1018-AGL-ZZ-ZZ-G-M-5310
FS1018-AGL-ZZ-ZZ-G-M-5410 | Gas Schematic | P01 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-04-07 | 1. Level 00 gas entry, high and low level vent grilles, low level only indicated 2. No CO2 sensors indicated on the drawing | TRUE | FS1018-AGL-ZZ-ZZ-G-M-5410 Gas Schematic | FS1018-AGL-ZZ-ZZ-G-M-5410
FS1018-AGL-ZZ-ZZ-G-M-5410 | Gas Schematic | P01 | In Progress | 2025-04-07 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-ZZ-G-M-5410 Gas Schematic | FS1018-AGL-ZZ-ZZ-G-M-5410
FS1018-AGL-ZZ-ZZ-G-M-5610 | Heating & Cooling Schematic Sheet 1 | P01 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-03-27 | Appreciate flowrates, pipesizes etc are on the heating calculations document but would expect these to be on the schematic | TRUE | FS1018-AGL-ZZ-ZZ-G-M-5610 Heating & Cooling Schematic Sheet 1 | FS1018-AGL-ZZ-ZZ-G-M-5610
FS1018-AGL-ZZ-ZZ-G-M-5610 | Heating & Cooling Schematic Sheet 1 | P01 | In Progress | 2025-03-27 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-ZZ-G-M-5610 Heating & Cooling Schematic Sheet 1 | FS1018-AGL-ZZ-ZZ-G-M-5610
FS1018-AGL-ZZ-ZZ-G-M-5611 | Heating & Cooling Schematic Sheet 2 | P01 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-03-27 | Appreciate flowrates, pipesizes etc are on the heating calculations document but would expect these to be on the schematic | TRUE | FS1018-AGL-ZZ-ZZ-G-M-5611 Heating & Cooling Schematic Sheet 2 | FS1018-AGL-ZZ-ZZ-G-M-5611
FS1018-AGL-ZZ-ZZ-G-M-5611 | Heating & Cooling Schematic Sheet 2 | P01 | In Progress | 2025-03-27 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-ZZ-G-M-5611 Heating & Cooling Schematic Sheet 2 | FS1018-AGL-ZZ-ZZ-G-M-5611
FS1018-AGL-ZZ-ZZ-G-M-5612 | Heating & Cooling Schematic Sheet 3 | P01 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-03-27 | Appreciate flowrates, pipesizes etc are on the heating calculations document but would expect these to be on the schematic | TRUE | FS1018-AGL-ZZ-ZZ-G-M-5612 Heating & Cooling Schematic Sheet 3 | FS1018-AGL-ZZ-ZZ-G-M-5612
FS1018-AGL-ZZ-ZZ-G-M-5612 | Heating & Cooling Schematic Sheet 3 | P01 | In Progress | 2025-03-27 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-ZZ-G-M-5612 Heating & Cooling Schematic Sheet 3 | FS1018-AGL-ZZ-ZZ-G-M-5612
FS1018-AGL-ZZ-ZZ-G-M-5613 | Heating & Cooling Schematic Sheet 4 | P01 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-03-27 | Appreciate flowrates, pipesizes etc are on the heating calculations document but would expect these to be on the schematic | TRUE | FS1018-AGL-ZZ-ZZ-G-M-5613 Heating & Cooling Schematic Sheet 4 | FS1018-AGL-ZZ-ZZ-G-M-5613
FS1018-AGL-ZZ-ZZ-G-M-5613 | Heating & Cooling Schematic Sheet 4 | P01 | In Progress | 2025-03-27 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-ZZ-G-M-5613 Heating & Cooling Schematic Sheet 4 | FS1018-AGL-ZZ-ZZ-G-M-5613
FS1018-AGL-ZZ-ZZ-G-M-5710 | Ventilation Schematic Sheet 1 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-ZZ-G-M-5710 Ventilation Schematic Sheet 1 | FS1018-AGL-ZZ-ZZ-G-M-5710
FS1018-AGL-ZZ-ZZ-G-M-5711 | Ventilation Schematic Sheet 2 | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-03-27 |  | TRUE | FS1018-AGL-ZZ-ZZ-G-M-5711 Ventilation Schematic Sheet 2 | FS1018-AGL-ZZ-ZZ-G-M-5711
FS1018-AGL-ZZ-ZZ-G-M-5812 | Plantroom Schematic | P01 | In Progress | 2025-03-14 | DFE Review | B - Partially Accepted with Comments | 2025-03-27 | CT HTG F&R flowrates don't align | TRUE | FS1018-AGL-ZZ-ZZ-G-M-5812 Plantroom Schematic | FS1018-AGL-ZZ-ZZ-G-M-5812
FS1018-AGL-ZZ-ZZ-G-M-5812 | Plantroom Schematic | P01 | In Progress | 2025-03-27 | Designer Response | Pending |  |  | TRUE | FS1018-AGL-ZZ-ZZ-G-M-5812 Plantroom Schematic | FS1018-AGL-ZZ-ZZ-G-M-5812
FS1018-AGL-ZZ-ZZ-M-Z-0001 | MEP Model Revit | P15 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-16 |  | TRUE | FS1018-AGL-ZZ-ZZ-M-Z-0001 MEP Model Revit | FS1018-AGL-ZZ-ZZ-M-Z-0001
FS1018-AGL-ZZ-ZZ-M-Z-0002 | MEP Model IFC | P15 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-16 |  | TRUE | FS1018-AGL-ZZ-ZZ-M-Z-0002 MEP Model IFC | FS1018-AGL-ZZ-ZZ-M-Z-0002
FS1018-AGL-ZZ-ZZ-M-Z-0003 | MEP Model NWC | P15 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-16 |  | TRUE | FS1018-AGL-ZZ-ZZ-M-Z-0003 MEP Model NWC | FS1018-AGL-ZZ-ZZ-M-Z-0003
FS1018-CPM-XX-XX-L-A-0001 | Schedule Of Accommodation | P06 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Please clarify why roof plant areas are included in the schedule. They are not internal spaces. 4.2 Proposed server room 2 is over area and the difference column has not been completed. Please clarify why this is over area. 4.3 Please clarify why the assembly hall is over the briefed area by 36m2. 4.4 Please clarify why GIFA is substantially over the briefed area | TRUE | FS1018-CPM-XX-XX-L-A-0001 Schedule Of Accommodation | FS1018-CPM-XX-XX-L-A-0001
FS1018-CPM-XX-XX-L-A-0001 | Schedule Of Accommodation | P06 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-XX-XX-L-A-0001 Schedule Of Accommodation | FS1018-CPM-XX-XX-L-A-0001
FS1018-CPM-XX-XX-T-A-0005 | Teaching Block Finishes | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Please indicate the DfE finishes references next to each item e.g. floor finish type F6.1 etc 4.2 This document makes reference to an IKO hot melt roof waterproofing system to all roof areas but section drawings refer to a Bauder system. Which one is correct? 4.3 Please indicate proposed RAL colours where currently stated TBC 4.4 Flooring indicated for showers is not suitable and dos not meet requirements of Technical Annex 2D. 4.5 Floor finishes do not match those indicated on floor finishes plans. Please coordinate the information. 4.6 Drinking fountain type does not meet the requirements of the DfE Output Specification 4.7 Please confirm that all sanitaryware meets the requirements of Technical Annex 2A 4.8 Outline spec refers to concealed cisterns but accessible WCs are indicated as having exposed cisterns. Please clarify | TRUE | FS1018-CPM-XX-XX-T-A-0005 Teaching Block Finishes | FS1018-CPM-XX-XX-T-A-0005
FS1018-CPM-XX-XX-T-A-0005 | Teaching Block Finishes | P04 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-XX-XX-T-A-0005 Teaching Block Finishes | FS1018-CPM-XX-XX-T-A-0005
FS1018-CPM-XX-XX-T-A-0010 | Outline Specification | P09 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Elevations refer to three brick colours yet outline spec only refers to 'stone-buff colour.' Actual brick types not specified 4.2 Outline spec refers to darker engineering brick beneath DPC level but this is not indicated on the elevation drawings. Is the spec or drawing correct? 4.3 Curtain walling spec refers to triple glazing yet this is not shown on any drawings. Is this correct? 4.4 Section 3.0 Roof. Please confirm that the roof spec meets the following requirement of Technical Annex 2C... 3.4.1 External surfaces of roofs shall be EU Class B roof (T4) to ENV 1187 Part 4: external fire exposure classification. 4.5 Section 4.3 Sanitary Cubicles. Please confirm that doors meet the requirements of Technical Annex 2A… 3.2.3 Inward opening doors shall be able to open outwards through use of an emergency releasable door hinge or a lift-off facility to facilitate emergency assistance to someone who has fallen against the door inside the cubicle (blocking the door from opening). 4.6 Section 4.4 / 4.5. Please add a note to the outline spec to cover splashbacks to hand driers as per Technical Annex 2D 9.2. | TRUE | FS1018-CPM-XX-XX-T-A-0010 Outline Specification | FS1018-CPM-XX-XX-T-A-0010
FS1018-CPM-XX-XX-T-A-0010 | Outline Specification | P09 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-XX-XX-T-A-0010 Outline Specification | FS1018-CPM-XX-XX-T-A-0010
FS1018-CPM-XX-XX-T-A-5001 | Stage 4 Report | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Section 1.07 community use plan diagram shows incorrect boundary of 'entrance zone 4.2 Section 6.04 shows 3d images of the main hall with lighting shown at what appears to be a low level not compliant with the minimum clear height requirements - please clarify. 4.3 Section 6.06 - image 9 is a repeat of image 3. 4.4 3D view in Section 8.03 shows mech vent clashing with glazing rather than meeting the louvred panel. 4.5 section 9.01 'accessible facilities' refers to clear circulation widths that are not actually achieved. | TRUE | FS1018-CPM-XX-XX-T-A-5001 Stage 4 Report | FS1018-CPM-XX-XX-T-A-5001
FS1018-CPM-XX-XX-T-A-5001 | Stage 4 Report | P01 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-XX-XX-T-A-5001 Stage 4 Report | FS1018-CPM-XX-XX-T-A-5001
FS1018-CPM-XX-XX-T-A-5002 | Design Development Report | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-04 | 4.1 Document will require updating once stage 4 comments are addressed to pick up various issues | TRUE | FS1018-CPM-XX-XX-T-A-5002 Design Development Report | FS1018-CPM-XX-XX-T-A-5002
FS1018-CPM-XX-XX-T-A-5002 | Design Development Report | P02 | In Progress | 2025-04-04 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-XX-XX-T-A-5002 Design Development Report | FS1018-CPM-XX-XX-T-A-5002
FS1018-CPM-XX-XX-T-A-5003 | Pre-Construction Information | P01 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-CPM-XX-XX-T-A-5003 Pre-Construction Information | FS1018-CPM-XX-XX-T-A-5003
FS1018-CPM-XX-ZZ-L-A-0000 | Building Model COBie Report | P25 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-16 | See Clarification for FS1018-MAJ-XX-XX-T-X-8001-AssetRegister-P02, On issued address new QC report needs to be issued. Please ensure that the Quality Control (QC) shows the output status for each COBie output reporting against the design criteria specified by the COBie schema | TRUE | FS1018-CPM-XX-ZZ-L-A-0000 Building Model COBie Report | FS1018-CPM-XX-ZZ-L-A-0000
FS1018-CPM-XX-ZZ-L-A-0000 | Building Model COBie Report | P25 | In Progress | 2025-04-16 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-XX-ZZ-L-A-0000 Building Model COBie Report | FS1018-CPM-XX-ZZ-L-A-0000
FS1018-CPM-ZZ-00-D-A-2001 | GA Proposed L00 Floor Plan | P17 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | note: drawing comments outstanding from stage 3 are numbered 3.x. New Stage 4 comments are numbered 4.x. 3.1 Review appropriateness of proposed kitchen layout and 4 spaces within. Locating them all to the north reduces the usable wall area for the kitchen layout. Also consider environmental health requirements for access to toilets an clean/dirty workstreams. Is it worth trying to cluster these uses either side of the external door? ...For example, to meet Food Hygiene Standards, a WC cannot be directly off food areas and therefore the WC needs to be separated off with an additional wall and door. 4.1 Door to Food Prep Room 1 needs to move over to avoid door furniture clashing with the column boxing as shown 4.2 Lockers not required. Please remove from the drawings/ FF&E. 4.3 Double doors to reception/ waiting area are shown as dual swing and clashing with corridor circulation. Please change to single swing so that they do not risk hitting persons in the main corridor. 4.4 Why are double doors to lobby 1 shown as dual swing? How does this work with the maglock/ access control strategy. We suggest changing to single swing open outwards. 4.5 Please confirm why the main entrance draught lobby has been increased in size to give access to the reception desk rather than the main reception desk being accessed via the waiting area 4.6 Please confirm why interview room 2 is not accessed from the secure lobby/ waiting area 4.7 Please indicate the required 465mm diameter standing space clear of the door swing as required by Approved Document T 4.8 Partition between music practice room and the main corridor does not meet the requirements of the Acoustic Report 4.9 How is the Control Room space accommodated in the plan? | TRUE | FS1018-CPM-ZZ-00-D-A-2001 GA Proposed L00 Floor Plan | FS1018-CPM-ZZ-00-D-A-2001
FS1018-CPM-ZZ-00-D-A-2001 | GA Proposed L00 Floor Plan | P17 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-00-D-A-2001 GA Proposed L00 Floor Plan | FS1018-CPM-ZZ-00-D-A-2001
FS1018-CPM-ZZ-00-D-A-2142 | Ground Edge Details | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Please include a key for the line types/ colours 4.2 Detail 1 annotates rockwool insulation at 125mm but there is a stray dimension of 100mm. Please correct 4.3 Detail 1 text refers to SFS but no SFS is drawn 4.4 Detail 2. Please clarify how the gas membrane is detailed at the perimeter of the building. " 4.5 Detail 2. Structural drawings indicate a 250mm thick suspended RC slab yet this drawing indicates a slab thickness of on 205mm. Please coordinate a step in the slab to accommodate the sports floor if required. 4.6 Detail 3. Curtain walling bottom transom and cill not detailed correctly | TRUE | FS1018-CPM-ZZ-00-D-A-2142 Ground Edge Details | FS1018-CPM-ZZ-00-D-A-2142
FS1018-CPM-ZZ-00-D-A-2142 | Ground Edge Details | P02 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-00-D-A-2142 Ground Edge Details | FS1018-CPM-ZZ-00-D-A-2142
FS1018-CPM-ZZ-00-D-A-2200 | Wall And Partition Types L00 | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Many of the wall type tags incorrectly annotate walls as having zero acoustic rating. 4.2 Partition between music practice room and the main corridor does not meet the requirements of the Acoustic Report | TRUE | FS1018-CPM-ZZ-00-D-A-2200 Wall And Partition Types L00 | FS1018-CPM-ZZ-00-D-A-2200
FS1018-CPM-ZZ-00-D-A-2200 | Wall And Partition Types L00 | P01 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-00-D-A-2200 Wall And Partition Types L00 | FS1018-CPM-ZZ-00-D-A-2200
FS1018-CPM-ZZ-00-D-A-2900 | Fire Strategy L00 | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Please clarify the requirement for the fire exits to the sports hall internal store. Are these 2no. external doors required? They will be blocked by equipment most of the time. 4.2 Please confirm that the required clear opening widths of final exit doors are actually achieved with the doors proposed. The openings look too small in many cases | TRUE | FS1018-CPM-ZZ-00-D-A-2900 Fire Strategy L00 | FS1018-CPM-ZZ-00-D-A-2900
FS1018-CPM-ZZ-00-D-A-2900 | Fire Strategy L00 | P04 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-00-D-A-2900 Fire Strategy L00 | FS1018-CPM-ZZ-00-D-A-2900
FS1018-CPM-ZZ-00-D-A-3001 | External Door Schedules Sheet 01 | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Please confirm that the required clear opening widths of final exit doors are actually achieved with the doors proposed. The openings look too small in many cases. | TRUE | FS1018-CPM-ZZ-00-D-A-3001 External Door Schedules Sheet 01 | FS1018-CPM-ZZ-00-D-A-3001
FS1018-CPM-ZZ-00-D-A-3001 | External Door Schedules Sheet 01 | P01 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-00-D-A-3001 External Door Schedules Sheet 01 | FS1018-CPM-ZZ-00-D-A-3001
FS1018-CPM-ZZ-00-D-A-3050 | Internal Doors Level 00 Sheet 01 | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 The drawings do not indicate the correct method of measuring clear opening widths in accordance with diagram 9 of Part M volume 2 | TRUE | FS1018-CPM-ZZ-00-D-A-3050 Internal Doors Level 00 Sheet 01 | FS1018-CPM-ZZ-00-D-A-3050
FS1018-CPM-ZZ-00-D-A-3050 | Internal Doors Level 00 Sheet 01 | P02 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-00-D-A-3050 Internal Doors Level 00 Sheet 01 | FS1018-CPM-ZZ-00-D-A-3050
FS1018-CPM-ZZ-00-D-A-3051 | Internal Doors Level 00 Sheet 02 | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 The drawings do not indicate the correct method of measuring clear opening widths in accordance with diagram 9 of Part M volume 2 | TRUE | FS1018-CPM-ZZ-00-D-A-3051 Internal Doors Level 00 Sheet 02 | FS1018-CPM-ZZ-00-D-A-3051
FS1018-CPM-ZZ-00-D-A-3051 | Internal Doors Level 00 Sheet 02 | P02 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-00-D-A-3051 Internal Doors Level 00 Sheet 02 | FS1018-CPM-ZZ-00-D-A-3051
FS1018-CPM-ZZ-00-D-A-3052 | Internal Doors Level 00 Sheet 03 | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 The drawings do not indicate the correct method of measuring clear opening widths in accordance with diagram 9 of Part M volume 2 | TRUE | FS1018-CPM-ZZ-00-D-A-3052 Internal Doors Level 00 Sheet 03 | FS1018-CPM-ZZ-00-D-A-3052
FS1018-CPM-ZZ-00-D-A-3052 | Internal Doors Level 00 Sheet 03 | P01 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-00-D-A-3052 Internal Doors Level 00 Sheet 03 | FS1018-CPM-ZZ-00-D-A-3052
FS1018-CPM-ZZ-00-D-A-3053 | Internal Doors Level 00 Sheet 04 | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 The drawings do not indicate the correct method of measuring clear opening widths in accordance with diagram 9 of Part M volume 2 4.2 Odd push plates shown to the double door | TRUE | FS1018-CPM-ZZ-00-D-A-3053 Internal Doors Level 00 Sheet 04 | FS1018-CPM-ZZ-00-D-A-3053
FS1018-CPM-ZZ-00-D-A-3053 | Internal Doors Level 00 Sheet 04 | P01 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-00-D-A-3053 Internal Doors Level 00 Sheet 04 | FS1018-CPM-ZZ-00-D-A-3053
FS1018-CPM-ZZ-00-D-A-3054 | Internal Doors Level 00 Sheet 05 | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 The drawings do not indicate the correct method of measuring clear opening widths in accordance with diagram 9 of Part M volume 2 4.2 Odd push plates shown to the double door | TRUE | FS1018-CPM-ZZ-00-D-A-3054 Internal Doors Level 00 Sheet 05 | FS1018-CPM-ZZ-00-D-A-3054
FS1018-CPM-ZZ-00-D-A-3054 | Internal Doors Level 00 Sheet 05 | P01 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-00-D-A-3054 Internal Doors Level 00 Sheet 05 | FS1018-CPM-ZZ-00-D-A-3054
FS1018-CPM-ZZ-00-D-A-3500 | Reflected Ceiling L00 | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Drawing is difficult to read due to MEP items visible that should not be displayed in a reflected ceiling plan. Please amend for further review 4.2 Area of ceiling missing to gridline 3 around main entrance area 4.3 DT workshop ceiling rafts appear to clash with ceiling grid to the rear of the space 4.4 Key shows ceiling type C2.2 as blue hatch but the plan shows this as black. Please ensure the plan and the key correlate. Blue would be easier to see | TRUE | FS1018-CPM-ZZ-00-D-A-3500 Reflected Ceiling L00 | FS1018-CPM-ZZ-00-D-A-3500
FS1018-CPM-ZZ-00-D-A-3500 | Reflected Ceiling L00 | P02 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-00-D-A-3500 Reflected Ceiling L00 | FS1018-CPM-ZZ-00-D-A-3500
FS1018-CPM-ZZ-00-D-A-6807 | Room Elevations Hygiene Room | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Drawing shows exposed pipework. Technical Annex 2D requires concealed or tamperproof. Please confirm proposals 4.2 Please confirm how the falls are achieved to the gulley. Drawing shows a completely flat floor 4.3 Please remove or correct the 'floor finishes plan' which currently provides no information on floor finishes | TRUE | FS1018-CPM-ZZ-00-D-A-6807 Room Elevations Hygiene Room | FS1018-CPM-ZZ-00-D-A-6807
FS1018-CPM-ZZ-00-D-A-6807 | Room Elevations Hygiene Room | P01 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-00-D-A-6807 Room Elevations Hygiene Room | FS1018-CPM-ZZ-00-D-A-6807
FS1018-CPM-ZZ-00-D-A-6808 | Room Elecations Pupil WC'S | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Drawing shows exposed pipework. Technical Annex 2D requires concealed or tamperproof. Please confirm proposals 4.2 Please remove or correct the ceiling plan which is unreadable at the moment. 4.3 Please remove or correct the 'floor finishes plan' which currently provides no information on floor finishes 4.4 Please indicate the required 465mm diameter standing space clear of the door swing as required by Approved Document T 4.5 Wash hand basin heights do not meet the height stated in Table 2 of Technical Annex 2A | TRUE | FS1018-CPM-ZZ-00-D-A-6808 Room Elecations Pupil WC'S | FS1018-CPM-ZZ-00-D-A-6808
FS1018-CPM-ZZ-00-D-A-6808 | Room Elecations Pupil WC'S | P01 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-00-D-A-6808 Room Elecations Pupil WC'S | FS1018-CPM-ZZ-00-D-A-6808
FS1018-CPM-ZZ-00-D-A-6809 | Room Elevations Pupils And Staff WC | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Drawing shows exposed pipework. Technical Annex 2D requires concealed or tamperproof. Please confirm proposals 4.2 Please remove or correct the ceiling plan which is unreadable at the moment. 4.3 Please remove or correct the 'floor finishes plan' which currently provides no information on floor finishes 4.4 Please indicate the required 465mm diameter standing space clear of the door swing as required by Approved Document T 4.5 Wash hand basin heights do not meet the height stated in Table 2 of Technical Annex 2A | TRUE | FS1018-CPM-ZZ-00-D-A-6809 Room Elevations Pupils And Staff WC | FS1018-CPM-ZZ-00-D-A-6809
FS1018-CPM-ZZ-00-D-A-6809 | Room Elevations Pupils And Staff WC | P01 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-00-D-A-6809 Room Elevations Pupils And Staff WC | FS1018-CPM-ZZ-00-D-A-6809
FS1018-CPM-ZZ-00-D-A-6810 | Room Elevations Accessible WC | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Drawing shows exposed pipework. Technical Annex 2D requires concealed or tamperproof. Please confirm proposals 4.2 Please remove or correct the ceiling plan which is unreadable at the moment. 4.3 Please remove or correct the 'floor finishes plan' which currently provides no information on floor finishes | TRUE | FS1018-CPM-ZZ-00-D-A-6810 Room Elevations Accessible WC | FS1018-CPM-ZZ-00-D-A-6810
FS1018-CPM-ZZ-00-D-A-6810 | Room Elevations Accessible WC | P01 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-00-D-A-6810 Room Elevations Accessible WC | FS1018-CPM-ZZ-00-D-A-6810
FS1018-CPM-ZZ-00-D-A-6811 | Room Elevations Changing Room | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Drawing shows exposed pipework. Technical Annex 2D requires concealed or tamperproof. Please confirm proposals 4.2 Please remove or correct the ceiling plan which is unreadable at the moment. 4.3 Please remove or correct the 'floor finishes plan' which currently provides no information on floor finishes 4.4 For WCs with doors opening inwards, please indicate the required 465mm diameter standing space clear of the door swing as required by Approved Document T 4.5 please add dimensions to the changing room benching so that the numbers of changing spaces can be reviewed. 4.6 Shower drainage currently indicates point drains to every other shower cubicle. This does not comply with the Technical Annex 2F section 12.2.9.3. 4.7 Drawings indicate that the shower cubicles are not full height. 4.8 Wash hand basin heights do not meet the height stated in Table 2 of Technical Annex 2A | TRUE | FS1018-CPM-ZZ-00-D-A-6811 Room Elevations Changing Room | FS1018-CPM-ZZ-00-D-A-6811
FS1018-CPM-ZZ-00-D-A-6811 | Room Elevations Changing Room | P02 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-00-D-A-6811 Room Elevations Changing Room | FS1018-CPM-ZZ-00-D-A-6811
FS1018-CPM-ZZ-00-D-A-6812 | Room Elevations Accessible Changing Room | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Drawing shows exposed pipework. Technical Annex 2D requires concealed or tamperproof. Please confirm proposals 4.2 Please confirm how the falls are achieved to the gulley. Drawing shows a completely flat floor 4.3 Please remove or correct the 'floor finishes plan' which currently provides no information on floor finishes 4.4 Please remove or correct the ceiling plan which is unreadable at the moment. 4.5 Door requires a horizontal grab rail in accordance with diagram 23 of Part M. | TRUE | FS1018-CPM-ZZ-00-D-A-6812 Room Elevations Accessible Changing Room | FS1018-CPM-ZZ-00-D-A-6812
FS1018-CPM-ZZ-00-D-A-6812 | Room Elevations Accessible Changing Room | P01 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-00-D-A-6812 Room Elevations Accessible Changing Room | FS1018-CPM-ZZ-00-D-A-6812
FS1018-CPM-ZZ-01-D-A-2002 | GA Proposed L01 Floor Plan | P16 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Medical Room is accessed off another room which is poor for pupil privacy. Please review 4.2 Please indicate clear width of all corridor spaces including alongside the light wells. 4.3 Please remove lockers. These are not to be supplied 4.5 Please review location of outward opening door the the accessible WC as the clear width of the corridor must not be affected by the door swing. 4.6 Please revise the view depth of the plan view so that the hall and sports hall are not indicated at this level. 4.7 Please confirm occupancy of the meeting room. It is a very large room for only 6 seats. 4.8 Façade setting out appears off as there is a thin section of brickwork alongside the window reveal to gridline S and 3 4.9 Door and FF&E not coordinated to Cleaners Store 3 4.10 Please add up arrows to all staircases | TRUE | FS1018-CPM-ZZ-01-D-A-2002 GA Proposed L01 Floor Plan | FS1018-CPM-ZZ-01-D-A-2002
FS1018-CPM-ZZ-01-D-A-2002 | GA Proposed L01 Floor Plan | P16 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-01-D-A-2002 GA Proposed L01 Floor Plan | FS1018-CPM-ZZ-01-D-A-2002
FS1018-CPM-ZZ-01-D-A-2201 | Wall And Partition Types L01 | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | 4.1 Many of the wall type tags incorrectly annotate walls as having zero acoustic rating. | TRUE | FS1018-CPM-ZZ-01-D-A-2201 Wall And Partition Types L01 | FS1018-CPM-ZZ-01-D-A-2201
FS1018-CPM-ZZ-01-D-A-2201 | Wall And Partition Types L01 | P01 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-01-D-A-2201 Wall And Partition Types L01 | FS1018-CPM-ZZ-01-D-A-2201
FS1018-CPM-ZZ-01-D-A-2250 | Patressing Plan For Typical Classroom | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 How does this comply with the pattressing requirement stated in Technical Annex 2D 3.1.1.f | TRUE | FS1018-CPM-ZZ-01-D-A-2250 Patressing Plan For Typical Classroom | FS1018-CPM-ZZ-01-D-A-2250
FS1018-CPM-ZZ-01-D-A-2250 | Patressing Plan For Typical Classroom | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-01-D-A-2250 Patressing Plan For Typical Classroom | FS1018-CPM-ZZ-01-D-A-2250
FS1018-CPM-ZZ-01-D-A-2251 | Patressing Plan For Art Room | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Patressing to elevation B misses the end of the wall mounted coat hooks | TRUE | FS1018-CPM-ZZ-01-D-A-2251 Patressing Plan For Art Room | FS1018-CPM-ZZ-01-D-A-2251
FS1018-CPM-ZZ-01-D-A-2251 | Patressing Plan For Art Room | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-01-D-A-2251 Patressing Plan For Art Room | FS1018-CPM-ZZ-01-D-A-2251
FS1018-CPM-ZZ-01-D-A-2901 | Fire Strategy L01 | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please annotate the evacuation lift 4.2 Lift car appears much larger than the minimum required by GDB 2.14.3.11 a. Please clarify 4.3 How does the fire strategy deal with the escape past the ventilation voids? | TRUE | FS1018-CPM-ZZ-01-D-A-2901 Fire Strategy L01 | FS1018-CPM-ZZ-01-D-A-2901
FS1018-CPM-ZZ-01-D-A-2901 | Fire Strategy L01 | P04 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-01-D-A-2901 Fire Strategy L01 | FS1018-CPM-ZZ-01-D-A-2901
FS1018-CPM-ZZ-01-D-A-3501 | Reflected Ceiling L01 | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Drawing is difficult to read due to MEP items visible that should not be displayed in a reflected ceiling plan. Please amend to allow further review 4.2 Along gridline 5, classroom ceiling rafts appear to clash with ceiling grid/ tiles. 4.3 Key shows ceiling type C2.2 as blue hatch but the plan shows this as black. Please ensure the plan and the key correlate. Blue would be easier to see | TRUE | FS1018-CPM-ZZ-01-D-A-3501 Reflected Ceiling L01 | FS1018-CPM-ZZ-01-D-A-3501
FS1018-CPM-ZZ-01-D-A-3501 | Reflected Ceiling L01 | P02 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-01-D-A-3501 Reflected Ceiling L01 | FS1018-CPM-ZZ-01-D-A-3501
FS1018-CPM-ZZ-01-D-A-6800 | Room Elevations Classroom | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please remove or correct the ceiling plan which is unreadable at the moment. 4.2 Please remove or correct the 'floor finishes plan' which currently provides to no information on floor finishes 4.3 Please indicate dimension to underside of ceiling rafts 4.4 3D view indicates an exposed vertical pipework drop that clashes with a desk" | TRUE | FS1018-CPM-ZZ-01-D-A-6800 Room Elevations Classroom | FS1018-CPM-ZZ-01-D-A-6800
FS1018-CPM-ZZ-01-D-A-6800 | Room Elevations Classroom | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-01-D-A-6800 Room Elevations Classroom | FS1018-CPM-ZZ-01-D-A-6800
FS1018-CPM-ZZ-02-D-A-2003 | GA Proposed L02 Floor Plan | P17 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please remove the visible steelwork to the assembly hall and to the sports hall roof areas. Assembly hall steel shows uncoordinated openings to roof vents. 4.2 Please indicate dimensions for clear width of corridors e.g. alongside the light wells and the appliance bay 4.3 For WCs, please indicate the required 465mm diameter standing space clear of the door swing as required by Approved Document T 4.4 Access to small group room looks very tight. Please review. Could the adjacent store be relocated to the alongside stair 4 at first floor level in a similar arrangement to the level 2 store alongside stairway 6. | TRUE | FS1018-CPM-ZZ-02-D-A-2003 GA Proposed L02 Floor Plan | FS1018-CPM-ZZ-02-D-A-2003
FS1018-CPM-ZZ-02-D-A-2003 | GA Proposed L02 Floor Plan | P17 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-02-D-A-2003 GA Proposed L02 Floor Plan | FS1018-CPM-ZZ-02-D-A-2003
FS1018-CPM-ZZ-02-D-A-2202 | Wall And Partition Types L02 | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Many of the wall type tags incorrectly annotate walls as having zero acoustic rating. | TRUE | FS1018-CPM-ZZ-02-D-A-2202 Wall And Partition Types L02 | FS1018-CPM-ZZ-02-D-A-2202
FS1018-CPM-ZZ-02-D-A-2202 | Wall And Partition Types L02 | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-02-D-A-2202 Wall And Partition Types L02 | FS1018-CPM-ZZ-02-D-A-2202
FS1018-CPM-ZZ-02-D-A-2902 | Fire Strategy L02 | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please annotate the evacuation lift 4.2 How does the fire strategy deal with the escape past the ventilation voids? | TRUE | FS1018-CPM-ZZ-02-D-A-2902 Fire Strategy L02 | FS1018-CPM-ZZ-02-D-A-2902
FS1018-CPM-ZZ-02-D-A-2902 | Fire Strategy L02 | P04 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-02-D-A-2902 Fire Strategy L02 | FS1018-CPM-ZZ-02-D-A-2902
FS1018-CPM-ZZ-02-D-A-3502 | Reflected Ceiling L02 | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Drawing is difficult to read due to MEP items visible that should not be displayed in a reflected ceiling plan. Please amend to allow further review 4.2 Classroom ceiling rafts appear to clash with ceiling grid/ tiles to the rear of each space. 4.3 Key shows ceiling type C2.2 as blue hatch but the plan shows this as black. Please ensure the plan and the key correlate. Blue would be easier to see | TRUE | FS1018-CPM-ZZ-02-D-A-3502 Reflected Ceiling L02 | FS1018-CPM-ZZ-02-D-A-3502
FS1018-CPM-ZZ-02-D-A-3502 | Reflected Ceiling L02 | P02 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-02-D-A-3502 Reflected Ceiling L02 | FS1018-CPM-ZZ-02-D-A-3502
FS1018-CPM-ZZ-RF-D-A-2023 | GA Proposed Roof Plan | P15 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 PV panels are not indicated to the full extent of where they could be accommodated. The roof needs to be optimised for PV panels before external canopies can be justified. 4.2 Gravel fire breaks are not shown. Please refer to Technical Annex 2C 3.2.10 (f). 4.3 Further details of the roof escape hatch are required to confirm compliance with Technical Annex 2C section 3.6. | TRUE | FS1018-CPM-ZZ-RF-D-A-2023 GA Proposed Roof Plan | FS1018-CPM-ZZ-RF-D-A-2023
FS1018-CPM-ZZ-RF-D-A-2023 | GA Proposed Roof Plan | P15 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-RF-D-A-2023 GA Proposed Roof Plan | FS1018-CPM-ZZ-RF-D-A-2023
FS1018-CPM-ZZ-RF-D-A-2144 | Roof Details Sheet 1 | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please add levels/ dimensions to all upstands and parapets 4.2 Details annotate 'levelling screed' to the roof - is this the correct type of screed to use on a sloping roof? 4.3 No indication of wall ties | TRUE | FS1018-CPM-ZZ-RF-D-A-2144 Roof Details Sheet 1 | FS1018-CPM-ZZ-RF-D-A-2144
FS1018-CPM-ZZ-RF-D-A-2144 | Roof Details Sheet 1 | P02 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-RF-D-A-2144 Roof Details Sheet 1 | FS1018-CPM-ZZ-RF-D-A-2144
FS1018-CPM-ZZ-RF-D-A-2145 | Roof Details Sheet 2 | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Details annotate 'levelling screed' to the roof - is this the correct type of screed to use on a sloping roof? 4.2 Drawing is marked as 'preliminary' - please clarify why this is included for stage 4 review | TRUE | FS1018-CPM-ZZ-RF-D-A-2145 Roof Details Sheet 2 | FS1018-CPM-ZZ-RF-D-A-2145
FS1018-CPM-ZZ-RF-D-A-2145 | Roof Details Sheet 2 | P02 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-RF-D-A-2145 Roof Details Sheet 2 | FS1018-CPM-ZZ-RF-D-A-2145
FS1018-CPM-ZZ-RF-D-A-2903 | Fire Strategy Rf | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please annotate each fire exit 4.2 Are sounders and or flashing beacons proposed at roof level? 4.3 PV panels on drawing and in the Key are different 4.4 Please indicate the gate to barrier around the rooflight means of escape as per Technical Annex 2C section 3.6 | TRUE | FS1018-CPM-ZZ-RF-D-A-2903 Fire Strategy Rf | FS1018-CPM-ZZ-RF-D-A-2903
FS1018-CPM-ZZ-RF-D-A-2903 | Fire Strategy Rf | P04 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-RF-D-A-2903 Fire Strategy Rf | FS1018-CPM-ZZ-RF-D-A-2903
FS1018-CPM-ZZ-RF-D-A-3100 | Rooflight Elevations Sheet 1 | P01 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-03 | no comments | TRUE | FS1018-CPM-ZZ-RF-D-A-3100 Rooflight Elevations Sheet 1 | FS1018-CPM-ZZ-RF-D-A-3100
FS1018-CPM-ZZ-RF-D-A-3101 | Rooflights And Hatch Plan | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 The key indicates that green dimensions are structural opening dimensions. For 1 and 2, how does the structure of each upstand work if the structure it outside of this as indicated i.e. how is the upstand structure supported | TRUE | FS1018-CPM-ZZ-RF-D-A-3101 Rooflights And Hatch Plan | FS1018-CPM-ZZ-RF-D-A-3101
FS1018-CPM-ZZ-RF-D-A-3101 | Rooflights And Hatch Plan | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-RF-D-A-3101 Rooflights And Hatch Plan | FS1018-CPM-ZZ-RF-D-A-3101
FS1018-CPM-ZZ-XX-D-A-2146 | 3D Section | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 The annotation refers to 100mm Knauf Rocksil Rainscreen Slab insulation with 50mm cavity but different insulation is indicated on other drawings (125mm Rockwool Nyroc with 25mm cavity) 4.2 Section through lift shaft does not indicate a lift pit or over-run. Are these not required?" | TRUE | FS1018-CPM-ZZ-XX-D-A-2146 3D Section | FS1018-CPM-ZZ-XX-D-A-2146
FS1018-CPM-ZZ-XX-D-A-2146 | 3D Section | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-XX-D-A-2146 3D Section | FS1018-CPM-ZZ-XX-D-A-2146
FS1018-CPM-ZZ-XX-D-A-2210 | Partition Detail Plans | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Details 4, 8 and 10 show only 3 sides of column encased with BG Firecase. Does this detail provide the required fire protection for the steelwork? 4.2 Detail 4 is not detailed to mitigate sound transfer between rooms and goes against the guidance in diagram ADT 3567/SK1 of the Acoustic Report i.e. external wall linings cannot continue from one room to another as this allows noise transfer. 4.3 Detail 3. How does single layer of mineral wall insulation to the SFS work around the cross bracing as shown? 4.4 Details 5 and 11. Does this detail provide the required fire protection for the steelwork? 4.5 Detail 9. Insulation clashing with cross bracing. | TRUE | FS1018-CPM-ZZ-XX-D-A-2210 Partition Detail Plans | FS1018-CPM-ZZ-XX-D-A-2210
FS1018-CPM-ZZ-XX-D-A-2210 | Partition Detail Plans | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-XX-D-A-2210 Partition Detail Plans | FS1018-CPM-ZZ-XX-D-A-2210
FS1018-CPM-ZZ-XX-L-A-0020 | CDM Design Risk Assessment | P03 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-CPM-ZZ-XX-L-A-0020 CDM Design Risk Assessment | FS1018-CPM-ZZ-XX-L-A-0020
FS1018-CPM-ZZ-ZZ-D-A-0050 | Circulation Strategy | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-04 | 4.1 Difficult to comment as not all dimensions are noted on the GA plans but in some cases the clear width indicated on this drawing (indicated in the key) does not match the actual clear width dimension indicated on the GA plan. | TRUE | FS1018-CPM-ZZ-ZZ-D-A-0050 Circulation Strategy | FS1018-CPM-ZZ-ZZ-D-A-0050
FS1018-CPM-ZZ-ZZ-D-A-0050 | Circulation Strategy | P03 | In Progress | 2025-04-04 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-0050 Circulation Strategy | FS1018-CPM-ZZ-ZZ-D-A-0050
FS1018-CPM-ZZ-ZZ-D-A-0051 | Zoning And Security Strategy | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Main entrance automatic doors, as referred to in the Outline Spec, not referenced on this plan. Security strategy needs to note this. 4.2 Access control is not shown to the double doors that lead from the main entrance waiting area into the main circulation corridor yet the two corridor doors are shown as having access control. Please clarify how the access control strategy allows visitors to wait in the waiting area without access to the corridor and the library. We suggest that the corridor access control is omitted and the access control required for the waiting area is added. 4.3 Doors that lead to roof access stairs and roof fire exit ladder are not shown as having a lock. | TRUE | FS1018-CPM-ZZ-ZZ-D-A-0051 Zoning And Security Strategy | FS1018-CPM-ZZ-ZZ-D-A-0051
FS1018-CPM-ZZ-ZZ-D-A-0051 | Zoning And Security Strategy | P03 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-0051 Zoning And Security Strategy | FS1018-CPM-ZZ-ZZ-D-A-0051
FS1018-CPM-ZZ-ZZ-D-A-0052 | Sanitary And Hygiene Strategy | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please indicate overall quantity of pupil WCs and overall quantity of staff WCs 4.2 Some drawings indicate the staff WC opposite the sick bay as being an accessible WC but this drawing shows it as not being accessible. Which is correct? 4.3 The layouts do not appear to comply with the handing requirements of Part M 5.10c. Please review | TRUE | FS1018-CPM-ZZ-ZZ-D-A-0052 Sanitary And Hygiene Strategy | FS1018-CPM-ZZ-ZZ-D-A-0052
FS1018-CPM-ZZ-ZZ-D-A-0052 | Sanitary And Hygiene Strategy | P03 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-0052 Sanitary And Hygiene Strategy | FS1018-CPM-ZZ-ZZ-D-A-0052
FS1018-CPM-ZZ-ZZ-D-A-0053 | Access And Maintenance Strategy | P05 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Hard standing area indicated around building perimeter is not actually provided on the landscape drawings 4.2 Please add a note to cover the maintenance strategy for non-accessible roof area over roof access stair 4.3 Please remove hatch to assembly hall and sports hall from the upper floors 4.4 Please list the kitchen fire shutter in section 4 of the scheduled tasks list | TRUE | FS1018-CPM-ZZ-ZZ-D-A-0053 Access And Maintenance Strategy | FS1018-CPM-ZZ-ZZ-D-A-0053
FS1018-CPM-ZZ-ZZ-D-A-0053 | Access And Maintenance Strategy | P05 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-0053 Access And Maintenance Strategy | FS1018-CPM-ZZ-ZZ-D-A-0053
FS1018-CPM-ZZ-ZZ-D-A-0054 | Cleaning And Maintenance Strategy | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 3.1 How are smaller areas of roof proposed to be accessed, cleaned and maintained? Roofs to: LRC, Sports stores, entrance canopy For example: roof over access stair. Please strategy for gutter and outlet inspection and cleaning, plus visual inspection of roof. 3.2 Need to indicate access and clearances around roof plant / PV's, as well as travel distances | TRUE | FS1018-CPM-ZZ-ZZ-D-A-0054 Cleaning And Maintenance Strategy | FS1018-CPM-ZZ-ZZ-D-A-0054
FS1018-CPM-ZZ-ZZ-D-A-0054 | Cleaning And Maintenance Strategy | P04 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-0054 Cleaning And Maintenance Strategy | FS1018-CPM-ZZ-ZZ-D-A-0054
FS1018-CPM-ZZ-ZZ-D-A-0060 | Proposed Room Cluster Diagram | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-03 | no comments | TRUE | FS1018-CPM-ZZ-ZZ-D-A-0060 Proposed Room Cluster Diagram | FS1018-CPM-ZZ-ZZ-D-A-0060
FS1018-CPM-ZZ-ZZ-D-A-2001 | GA Proposed Section Aa, Bb, Cc, Dd | P08 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 3.3 Please show proposed parapet levels to AOD 4.1 Main hall appears to show lighting compromising the clear height of the hall 4.2 Sections incorrectly show the topography as completely flat and level with internal FFL. 4.3 Clear height requirement for sports hall is not achieved. | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2001 GA Proposed Section Aa, Bb, Cc, Dd | FS1018-CPM-ZZ-ZZ-D-A-2001
FS1018-CPM-ZZ-ZZ-D-A-2001 | GA Proposed Section Aa, Bb, Cc, Dd | P08 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2001 GA Proposed Section Aa, Bb, Cc, Dd | FS1018-CPM-ZZ-ZZ-D-A-2001
FS1018-CPM-ZZ-ZZ-D-A-2002 | GA Proposed Section EE | P06 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Main hall appears to show lighting compromising the clear height of the hall 4.2 Section incorrectly shows the topography as completely flat and level with internal FFL. 4.3 Clear height requirement for sports hall is not achieved. | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2002 GA Proposed Section EE | FS1018-CPM-ZZ-ZZ-D-A-2002
FS1018-CPM-ZZ-ZZ-D-A-2002 | GA Proposed Section EE | P06 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2002 GA Proposed Section EE | FS1018-CPM-ZZ-ZZ-D-A-2002
FS1018-CPM-ZZ-ZZ-D-A-2010 | GA Proposed Elevations Sheet 1 | P08 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 3.1 Consider terminating curtain walling at half landing instead of running down to L00 level if this area under stair will be out of sight and inaccessible? Not best use of £ also consider robustness requirements of ER's (GDB and TA 2C) 4.1 are changing room doors proposed to be fully glazed? Consider the use of glazing film/ graphics/ signage to denote male and female changing rooms and also aid privacy 4.2 how is lighting over the main hall external doors going to be fixed to the glazing?" 4.3 Louvred panels to window system have very mixed appearance potentially caused my a clash from the MEP model 4.4 No brickwork movement joints indicated. 4.5 Are the glazed overpanels to sports hall store doors actually required? | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2010 GA Proposed Elevations Sheet 1 | FS1018-CPM-ZZ-ZZ-D-A-2010
FS1018-CPM-ZZ-ZZ-D-A-2010 | GA Proposed Elevations Sheet 1 | P08 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2010 GA Proposed Elevations Sheet 1 | FS1018-CPM-ZZ-ZZ-D-A-2010
FS1018-CPM-ZZ-ZZ-D-A-2011 | GA Proposed Elevations Sheet 02 | P06 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 3.1 Consider terminating curtain walling at half landing instead of running down to L00 level if this area under stair will be out of sight and inaccessible? Not best use of £ also consider robustness requirements of ER's (GDB and TA 2C) 4.1 are changing room doors proposed to be fully glazed? Consider the use of glazing film/ graphics/ signage to denote male and female changing rooms and also aid privacy 4.2 how is lighting over the main hall external doors going to be fixed to the glazing? 4.3 Louvred panels to window system have very mixed appearance potentially caused my a clash from the MEP model 4.4 No brickwork movement joints indicated. 4.5 Are the glazed overpanels to sports hall store doors actually required? " | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2011 GA Proposed Elevations Sheet 02 | FS1018-CPM-ZZ-ZZ-D-A-2011
FS1018-CPM-ZZ-ZZ-D-A-2011 | GA Proposed Elevations Sheet 02 | P06 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2011 GA Proposed Elevations Sheet 02 | FS1018-CPM-ZZ-ZZ-D-A-2011
FS1018-CPM-ZZ-ZZ-D-A-2012 | GA Proposed Elevations Sheet 03 | P05 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 3.1 Is signage on canopy sufficiently sized and contrasting for the person on the ground looking upwards? 4.1 Louvred panels to window system have very mixed appearance potentially caused my a clash from the MEP model 4.2 how is lighting over the main entrance external doors going to be fixed to the glazing? 4.3 No brickwork movement joints indicated. | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2012 GA Proposed Elevations Sheet 03 | FS1018-CPM-ZZ-ZZ-D-A-2012
FS1018-CPM-ZZ-ZZ-D-A-2012 | GA Proposed Elevations Sheet 03 | P05 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2012 GA Proposed Elevations Sheet 03 | FS1018-CPM-ZZ-ZZ-D-A-2012
FS1018-CPM-ZZ-ZZ-D-A-2025 | Hazard Identification Plan | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please indicate the working at height/ falls hazard of high level maintenance in hall spaces | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2025 Hazard Identification Plan | FS1018-CPM-ZZ-ZZ-D-A-2025
FS1018-CPM-ZZ-ZZ-D-A-2025 | Hazard Identification Plan | P02 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2025 Hazard Identification Plan | FS1018-CPM-ZZ-ZZ-D-A-2025
FS1018-CPM-ZZ-ZZ-D-A-2031 | Internal Views | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Lighting to main hall is too low and impacts on the clear height requirement | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2031 Internal Views | FS1018-CPM-ZZ-ZZ-D-A-2031
FS1018-CPM-ZZ-ZZ-D-A-2031 | Internal Views | P03 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2031 Internal Views | FS1018-CPM-ZZ-ZZ-D-A-2031
FS1018-CPM-ZZ-ZZ-D-A-2032 | External Views | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 PV panels shown different in some views. Some are shown north facing. 4.2 Principal Entrance image shows ductwork clashing with louvred panels and lighting fixed to glass over main entrance doors. | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2032 External Views | FS1018-CPM-ZZ-ZZ-D-A-2032
FS1018-CPM-ZZ-ZZ-D-A-2032 | External Views | P03 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2032 External Views | FS1018-CPM-ZZ-ZZ-D-A-2032
FS1018-CPM-ZZ-ZZ-D-A-2040 | Lock Suiting Strategy | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Access control required to waiting area door to corridor but not likely to be required to the two sets of double doors within the corridor. Please clarify/ revise 4.2 Exam office and exam store shown on incorrect lock suite | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2040 Lock Suiting Strategy | FS1018-CPM-ZZ-ZZ-D-A-2040
FS1018-CPM-ZZ-ZZ-D-A-2040 | Lock Suiting Strategy | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2040 Lock Suiting Strategy | FS1018-CPM-ZZ-ZZ-D-A-2040
FS1018-CPM-ZZ-ZZ-D-A-2140 | Construction Building Sections Sheet 1 | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 3.1 Detail 2 (section B-B): Is there barrier matting here? 3.2 Are top hung opening light's automated? Or teleflex? 4.1 Section A-A shows top hung window in ceiling void 4.2 Levelling screed is not correct type of screed to lay on a sloping roof 4.3 Section B-B shows double glazed curtain walling but specification refers to trip glazing. 4.4 Section B-B annotates 'recessed concrete slab' to accommodate spring floor build up but this is not shown on the Structural Engineers information. Please coordinate 4.5 Levels not indicated for parapets 4.6 No mention of wall ties for brickwork outer leaf | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2140 Construction Building Sections Sheet 1 | FS1018-CPM-ZZ-ZZ-D-A-2140
FS1018-CPM-ZZ-ZZ-D-A-2140 | Construction Building Sections Sheet 1 | P04 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2140 Construction Building Sections Sheet 1 | FS1018-CPM-ZZ-ZZ-D-A-2140
FS1018-CPM-ZZ-ZZ-D-A-2141 | Construction Building Sections Sheet 2 | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Does this height of brickwork require a shelf angle/ masonry support angle? 4.2 No mention of wall ties for brickwork outer leaf 4.3 Section shows a recess in the ground floor slab rather than a stepped slab. Neither a recess or a stepped slab are shown in the Structural Engineers information. | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2141 Construction Building Sections Sheet 2 | FS1018-CPM-ZZ-ZZ-D-A-2141
FS1018-CPM-ZZ-ZZ-D-A-2141 | Construction Building Sections Sheet 2 | P02 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2141 Construction Building Sections Sheet 2 | FS1018-CPM-ZZ-ZZ-D-A-2141
FS1018-CPM-ZZ-ZZ-D-A-2143 | External Wall Details Sheet 1 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 How is fire protection to the steelwork achieved? | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2143 External Wall Details Sheet 1 | FS1018-CPM-ZZ-ZZ-D-A-2143
FS1018-CPM-ZZ-ZZ-D-A-2143 | External Wall Details Sheet 1 | P03 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2143 External Wall Details Sheet 1 | FS1018-CPM-ZZ-ZZ-D-A-2143
FS1018-CPM-ZZ-ZZ-D-A-2144 | External Wall Details Sheet 2 | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 How is fire protection to the steelwork achieved? | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2144 External Wall Details Sheet 2 | FS1018-CPM-ZZ-ZZ-D-A-2144
FS1018-CPM-ZZ-ZZ-D-A-2144 | External Wall Details Sheet 2 | P02 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2144 External Wall Details Sheet 2 | FS1018-CPM-ZZ-ZZ-D-A-2144
FS1018-CPM-ZZ-ZZ-D-A-2401 | Typical Staircase Sheet 01 | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please confirm that the curtain walling system achieves the actual clear opening width required for the final exit | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2401 Typical Staircase Sheet 01 | FS1018-CPM-ZZ-ZZ-D-A-2401
FS1018-CPM-ZZ-ZZ-D-A-2401 | Typical Staircase Sheet 01 | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2401 Typical Staircase Sheet 01 | FS1018-CPM-ZZ-ZZ-D-A-2401
FS1018-CPM-ZZ-ZZ-D-A-2402 | Typical Staircase Sheet 02 | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 bottom landing for roof access stair is less than the stair width. Does this meet Part K requirements | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2402 Typical Staircase Sheet 02 | FS1018-CPM-ZZ-ZZ-D-A-2402
FS1018-CPM-ZZ-ZZ-D-A-2402 | Typical Staircase Sheet 02 | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2402 Typical Staircase Sheet 02 | FS1018-CPM-ZZ-ZZ-D-A-2402
FS1018-CPM-ZZ-ZZ-D-A-2403 | Typical Staircase Sheet 03 | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 How are the exposed steel beams and the back of the curtain walling spandrel panels proposed to be finished? | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2403 Typical Staircase Sheet 03 | FS1018-CPM-ZZ-ZZ-D-A-2403
FS1018-CPM-ZZ-ZZ-D-A-2403 | Typical Staircase Sheet 03 | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2403 Typical Staircase Sheet 03 | FS1018-CPM-ZZ-ZZ-D-A-2403
FS1018-CPM-ZZ-ZZ-D-A-2404 | Typical Staircase Sheet 04 | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 How are the exposed steel beams and the back of the curtain walling spandrel panels proposed to be finished? | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2404 Typical Staircase Sheet 04 | FS1018-CPM-ZZ-ZZ-D-A-2404
FS1018-CPM-ZZ-ZZ-D-A-2404 | Typical Staircase Sheet 04 | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2404 Typical Staircase Sheet 04 | FS1018-CPM-ZZ-ZZ-D-A-2404
FS1018-CPM-ZZ-ZZ-D-A-2405 | Typical Staircase Sheet 05 | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 How are the exposed steel beams and the back of the curtain walling spandrel panels proposed to be finished? 4.2 How are the handrails supported alongside the curtain walling? | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2405 Typical Staircase Sheet 05 | FS1018-CPM-ZZ-ZZ-D-A-2405
FS1018-CPM-ZZ-ZZ-D-A-2405 | Typical Staircase Sheet 05 | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-2405 Typical Staircase Sheet 05 | FS1018-CPM-ZZ-ZZ-D-A-2405
FS1018-CPM-ZZ-ZZ-D-A-3002 | External Door Schedues Sheet 02 | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Some door types have structural opening widths and or heights that are not brick dimensions. How does this work? | TRUE | FS1018-CPM-ZZ-ZZ-D-A-3002 External Door Schedues Sheet 02 | FS1018-CPM-ZZ-ZZ-D-A-3002
FS1018-CPM-ZZ-ZZ-D-A-3002 | External Door Schedues Sheet 02 | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-3002 External Door Schedues Sheet 02 | FS1018-CPM-ZZ-ZZ-D-A-3002
FS1018-CPM-ZZ-ZZ-D-A-3010 | Curtain Wall Panelling Elevations Sheet 01 | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Curtain wall B has a structural opening height that is not a brick dim. How does this work? | TRUE | FS1018-CPM-ZZ-ZZ-D-A-3010 Curtain Wall Panelling Elevations Sheet 01 | FS1018-CPM-ZZ-ZZ-D-A-3010
FS1018-CPM-ZZ-ZZ-D-A-3010 | Curtain Wall Panelling Elevations Sheet 01 | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-3010 Curtain Wall Panelling Elevations Sheet 01 | FS1018-CPM-ZZ-ZZ-D-A-3010
FS1018-CPM-ZZ-ZZ-D-A-3011 | Curtain Wall Panelling Elevations Sheet 02 | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Curtain wall E has a structural opening height and width that is not a brick dim. How does this work? | TRUE | FS1018-CPM-ZZ-ZZ-D-A-3011 Curtain Wall Panelling Elevations Sheet 02 | FS1018-CPM-ZZ-ZZ-D-A-3011
FS1018-CPM-ZZ-ZZ-D-A-3011 | Curtain Wall Panelling Elevations Sheet 02 | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-3011 Curtain Wall Panelling Elevations Sheet 02 | FS1018-CPM-ZZ-ZZ-D-A-3011
FS1018-CPM-ZZ-ZZ-D-A-3020 | External Windows Elevation And Schedule | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Is window type 04 actually used? The schedule suggests not 4.2 Is window type 03 clear glazing for the server room? Does this create unwanted solar gain and potential overheating issues? 4.3 Schedule for window type 5 is off the page 4.4 Cill heights in schedules refer to 900mm but there is a stray red dimension of 1050mm that is noted as 'sill height' - is this actually the glazing height. Please clarify 4.5 Do high level opening windows have a teleflex? | TRUE | FS1018-CPM-ZZ-ZZ-D-A-3020 External Windows Elevation And Schedule | FS1018-CPM-ZZ-ZZ-D-A-3020
FS1018-CPM-ZZ-ZZ-D-A-3020 | External Windows Elevation And Schedule | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-3020 External Windows Elevation And Schedule | FS1018-CPM-ZZ-ZZ-D-A-3020
FS1018-CPM-ZZ-ZZ-D-A-3021 | Internal Glazed Panel Elevations And Schedule | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please clarify the design intent for glazed screen type 06? What it’s the purpose of this and how does it work with the servery fire shutter? 4.2 What are the fire and acoustic requirements? | TRUE | FS1018-CPM-ZZ-ZZ-D-A-3021 Internal Glazed Panel Elevations And Schedule | FS1018-CPM-ZZ-ZZ-D-A-3021
FS1018-CPM-ZZ-ZZ-D-A-3021 | Internal Glazed Panel Elevations And Schedule | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-3021 Internal Glazed Panel Elevations And Schedule | FS1018-CPM-ZZ-ZZ-D-A-3021
FS1018-CPM-ZZ-ZZ-D-A-3055 | Internal Doors Level 00 Sheet 06 | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 The drawings do not indicated the correct method of measuring clear opening widths in accordance with diagram 9 of Part M volume 2 | TRUE | FS1018-CPM-ZZ-ZZ-D-A-3055 Internal Doors Level 00 Sheet 06 | FS1018-CPM-ZZ-ZZ-D-A-3055
FS1018-CPM-ZZ-ZZ-D-A-3055 | Internal Doors Level 00 Sheet 06 | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-3055 Internal Doors Level 00 Sheet 06 | FS1018-CPM-ZZ-ZZ-D-A-3055
FS1018-CPM-ZZ-ZZ-D-A-3062 | Window Schedule | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Structural opening dimensions are not all brick dims. How does this work? | TRUE | FS1018-CPM-ZZ-ZZ-D-A-3062 Window Schedule | FS1018-CPM-ZZ-ZZ-D-A-3062
FS1018-CPM-ZZ-ZZ-D-A-3062 | Window Schedule | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-3062 Window Schedule | FS1018-CPM-ZZ-ZZ-D-A-3062
FS1018-CPM-ZZ-ZZ-D-A-4001 | GA Wall Finishes Strategy | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please specify wall finishes for the spaces currently noted as 'contractor to specify' 4.2 Please clarify the proposal for wall finish type W3.2. The key refers to a brush applied finish but also refers to a 'Hygenik H Panel' and an eggshell paint finish 4.3 Please clarify the proposed finishes to the hygiene room and the changing rooms/ showers. The key refers to ceramic tiling to showers but does not define the extent 4.4 Does the catering kitchen/ food prep room comply with Technical Annex 2D paragraph 9.1.23 4.5 Please add a key to explain the blue dashed lines. If these are to denote splashbacks, please confirm that they meet Technical Annex 2D section 9.2. 4.6 Please include proposals for wall finishes to the corridor light wells. The wall finishes would need to match the corridors but the plans currently just state 'n/a' 4.7 Sports hall acoustic wall finishes appear to measure 2400mm in height and are set 2400mm from FFL. Please clarify that this follows the recommendations of the acoustician as the Acoustic Strategy Report refers to perforated panels from FFL up to 3000mm height. 4.8 Both the wall types and wall finishes plans do not show how the exam store complies with JCQ requirements for security measures. Please refer to GDB 2.3.19.2 | TRUE | FS1018-CPM-ZZ-ZZ-D-A-4001 GA Wall Finishes Strategy | FS1018-CPM-ZZ-ZZ-D-A-4001
FS1018-CPM-ZZ-ZZ-D-A-4001 | GA Wall Finishes Strategy | P04 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-4001 GA Wall Finishes Strategy | FS1018-CPM-ZZ-ZZ-D-A-4001
FS1018-CPM-ZZ-ZZ-D-A-4004 | GA Floor Finishes Strategy | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please confirm the proposals for floor type F6.1 i.e. timber or vinyl top surface/ A3 or A4 area elastic rating/ product and thickness 4.2 Please confirm the proposals for floor type F6.2h i.e. timber or vinyl top surface/ A3 or A4 area elastic rating/ product and thickness 4.3 Please confirm proposals for the flooring currently noted as 'contractor to specify' 4.4 Please clarify the proposals for floor type F7.3h noting that the text currently in the key would result in non-compliant flooring to the changing rooms/ showers 4.5 Please confirm proposals for the flooring currently noted as 'contractor to specify' 4.6 Please remove the colour from the roof areas, MEP risers and light wells as this is misleading 4.7 Please clarify the proposals for skirting. This drawings states pencil round skirting but External Wall details show chamfered. 4.8 Please confirm floor finishes proposals for the lift and stairs. 4.9 Please confirm how and why the floor finish works to the 'control room' within the bleacher seating area 4.10 Please confirm how the two areas are barrier matting are incorporated in the assembly hall floor finish 4.11 Please add barrier matting to the 2no. external doors to the stair cores at ground floor level 4.12 Please confirm product proposed for barrier matting 4.13 Please review rooms where there is a transition in floor finish i.e. pastoral room and SENCo office at first floor level, staff work room at second floor level and ground floor premises office and proposed one floor finish. To be raised as a derogation to be agreed. | TRUE | FS1018-CPM-ZZ-ZZ-D-A-4004 GA Floor Finishes Strategy | FS1018-CPM-ZZ-ZZ-D-A-4004
FS1018-CPM-ZZ-ZZ-D-A-4004 | GA Floor Finishes Strategy | P04 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-4004 GA Floor Finishes Strategy | FS1018-CPM-ZZ-ZZ-D-A-4004
FS1018-CPM-ZZ-ZZ-D-A-6601 | Lift Pit Details | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Lift car is oversized compared to the DfE minimum size required by GDB 2.14.3.11 a. Please clarify 4.2 Is a lift over-run required? 4.3 Is the liftshaft blockwork actually being design by a specialist subcontractor as noted on the drawing? 4.4 Is the lift shaft blockwork actually constructed off the screed as drawn? 4.5 Are two forms of waterproofing proposed for the lift pit? To achieve a Grade 3 environment 4.6 The 'ground edge details' indicate a gas membrane. How is the detailed around the lift pit? | TRUE | FS1018-CPM-ZZ-ZZ-D-A-6601 Lift Pit Details | FS1018-CPM-ZZ-ZZ-D-A-6601
FS1018-CPM-ZZ-ZZ-D-A-6601 | Lift Pit Details | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-6601 Lift Pit Details | FS1018-CPM-ZZ-ZZ-D-A-6601
FS1018-CPM-ZZ-ZZ-D-A-6801 | Room Elevations Assembly Dining Sheet 1 | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please remove or correct the ceiling plan which is unreadable at the moment. 4.2 Please remove or correct the 'floor finishes plan' which currently provides to no information on floor finishes 4.3 Lighting indicated in the 3d image is too low and conflicts with the minimum clear height requirement 4.4 Please clarify how access to the lighting and audio controls unit can be accessed. Looks like it is not accessible both when the bleacher seating is in use and also when the bleacher seating is not in use. | TRUE | FS1018-CPM-ZZ-ZZ-D-A-6801 Room Elevations Assembly Dining Sheet 1 | FS1018-CPM-ZZ-ZZ-D-A-6801
FS1018-CPM-ZZ-ZZ-D-A-6801 | Room Elevations Assembly Dining Sheet 1 | P02 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-6801 Room Elevations Assembly Dining Sheet 1 | FS1018-CPM-ZZ-ZZ-D-A-6801
FS1018-CPM-ZZ-ZZ-D-A-6802 | Room Elevations Assembly Dining Sheet 2 | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Lighting to main hall is too low and impacts on the clear height requirement 4.2 Exposed pipework along gridline 6A 4.3 How is the air curtain unit fixed. Can this be coordinated with the exposed steelwork so that the air curtains have something to fix to, the pipework could be boxed out and the steelwork hidden on the outside with a spandrel in the curtain walling 4.4 Radiator positions appear to clash with bleacher seating | TRUE | FS1018-CPM-ZZ-ZZ-D-A-6802 Room Elevations Assembly Dining Sheet 2 | FS1018-CPM-ZZ-ZZ-D-A-6802
FS1018-CPM-ZZ-ZZ-D-A-6802 | Room Elevations Assembly Dining Sheet 2 | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-6802 Room Elevations Assembly Dining Sheet 2 | FS1018-CPM-ZZ-ZZ-D-A-6802
FS1018-CPM-ZZ-ZZ-D-A-6803 | Room Elevations Sports Hall Sheet 1 | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please add dimensions to the court markings setting out 4.2 Please indicate the location of the rooflights on the ceiling plan and annotate the items 4.3 Is the sports hall lighting over the badminton courts rather than in between the courts 4.4 In reality will the cricket nets clash with the basketball back board as drawn? | TRUE | FS1018-CPM-ZZ-ZZ-D-A-6803 Room Elevations Sports Hall Sheet 1 | FS1018-CPM-ZZ-ZZ-D-A-6803
FS1018-CPM-ZZ-ZZ-D-A-6803 | Room Elevations Sports Hall Sheet 1 | P02 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-6803 Room Elevations Sports Hall Sheet 1 | FS1018-CPM-ZZ-ZZ-D-A-6803
FS1018-CPM-ZZ-ZZ-D-A-6804 | Room Elevations Sports Hall Sheet 2 | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Floor finishes plan provides no information on floor finishes. Is this drawing required being as there is a separate floor finishes plan intended to provide information on floor finishes? 4.2 3D view indicates clash between dividing curtain and what looks like containment / cable tray. | TRUE | FS1018-CPM-ZZ-ZZ-D-A-6804 Room Elevations Sports Hall Sheet 2 | FS1018-CPM-ZZ-ZZ-D-A-6804
FS1018-CPM-ZZ-ZZ-D-A-6804 | Room Elevations Sports Hall Sheet 2 | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-6804 Room Elevations Sports Hall Sheet 2 | FS1018-CPM-ZZ-ZZ-D-A-6804
FS1018-CPM-ZZ-ZZ-D-A-6805 | Room Elevations Sports Hall Sheet 3 | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please add a key for the location of each section. 4.2 Please move section 3 so that each room elevation displays properly. This appears to show the cricket nets on gridline S. Fire exit doors on gridline Y are not visible. 4.3 The drawing indicates clash between dividing curtain and what looks like containment / cable tray. 4.4 Section 4. Can the first floor glazed screen line up with the door below? 4.5 Clear sports hall height of 7500mm has not been achieved. Currently obstructed by steelwork and MEP | TRUE | FS1018-CPM-ZZ-ZZ-D-A-6805 Room Elevations Sports Hall Sheet 3 | FS1018-CPM-ZZ-ZZ-D-A-6805
FS1018-CPM-ZZ-ZZ-D-A-6805 | Room Elevations Sports Hall Sheet 3 | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-6805 Room Elevations Sports Hall Sheet 3 | FS1018-CPM-ZZ-ZZ-D-A-6805
FS1018-CPM-ZZ-ZZ-D-A-6806 | Room Elevations Sports Hall Acoustic Panel Set Out | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please mark the elevations on the plan" 4.2 How does the panelling work around doors? No doors are indicated 4.3 Extent of acoustic panels does not match the acoustic report recommendations | TRUE | FS1018-CPM-ZZ-ZZ-D-A-6806 Room Elevations Sports Hall Acoustic Panel Set Out | FS1018-CPM-ZZ-ZZ-D-A-6806
FS1018-CPM-ZZ-ZZ-D-A-6806 | Room Elevations Sports Hall Acoustic Panel Set Out | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-6806 Room Elevations Sports Hall Acoustic Panel Set Out | FS1018-CPM-ZZ-ZZ-D-A-6806
FS1018-CPM-ZZ-ZZ-D-A-6813 | Room Elevations Pupil WC'S L01 And L02 | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Floor finishes plan provides no information on floor finishes. Is this drawing required being as there is a separate floor finishes plan intended to provide information on floor finishes? 4.2 Please indicate the required 465mm diameter standing space clear of the door swing as required by Approved Document T 4.3 Drawings appear to show 2no. hand dryers per WC. One at high level 4.4 Reflected ceiling plan is not readable 4.5 Wash hand basin heights do not meet the height stated in Table 2 of Technical Annex 2A | TRUE | FS1018-CPM-ZZ-ZZ-D-A-6813 Room Elevations Pupil WC'S L01 And L02 | FS1018-CPM-ZZ-ZZ-D-A-6813
FS1018-CPM-ZZ-ZZ-D-A-6813 | Room Elevations Pupil WC'S L01 And L02 | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-D-A-6813 Room Elevations Pupil WC'S L01 And L02 | FS1018-CPM-ZZ-ZZ-D-A-6813
FS1018-CPM-ZZ-ZZ-L-A-0001 | Clash Report | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 The report identifies 560 pages of clashes but contains no information on the proposed remediation or 'owners' of each clash. | TRUE | FS1018-CPM-ZZ-ZZ-L-A-0001 Clash Report | FS1018-CPM-ZZ-ZZ-L-A-0001
FS1018-CPM-ZZ-ZZ-L-A-0001 | Clash Report | P03 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-L-A-0001 Clash Report | FS1018-CPM-ZZ-ZZ-L-A-0001
FS1018-CPM-ZZ-ZZ-L-A-3060 | Internal Door Schedule | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Schedule goes off the page. Is part of it missing? 4.2 Please clarify the difference between the ratings and performance | TRUE | FS1018-CPM-ZZ-ZZ-L-A-3060 Internal Door Schedule | FS1018-CPM-ZZ-ZZ-L-A-3060
FS1018-CPM-ZZ-ZZ-L-A-3060 | Internal Door Schedule | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-L-A-3060 Internal Door Schedule | FS1018-CPM-ZZ-ZZ-L-A-3060
FS1018-CPM-ZZ-ZZ-L-A-3061 | External Door Schedule | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Please clarify why some doors are noted as requiring a 30min fire rating and 30dB acoustic rating 4.2 Structural opening dimensions are not all brick dims. How does this work? | TRUE | FS1018-CPM-ZZ-ZZ-L-A-3061 External Door Schedule | FS1018-CPM-ZZ-ZZ-L-A-3061
FS1018-CPM-ZZ-ZZ-L-A-3061 | External Door Schedule | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-L-A-3061 External Door Schedule | FS1018-CPM-ZZ-ZZ-L-A-3061
FS1018-CPM-ZZ-ZZ-M-A-0002 | Federated Model | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-16 | Not all disciplines models have been intergratd into the Federated Model (catering & Civil) | TRUE | FS1018-CPM-ZZ-ZZ-M-A-0002 Federated Model | FS1018-CPM-ZZ-ZZ-M-A-0002
FS1018-CPM-ZZ-ZZ-M-A-0002 | Federated Model | P03 | In Progress | 2025-04-16 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-M-A-0002 Federated Model | FS1018-CPM-ZZ-ZZ-M-A-0002
FS1018-CPM-ZZ-ZZ-M-A-0003 | Architectural Model NWC | P25 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-16 |  | TRUE | FS1018-CPM-ZZ-ZZ-M-A-0003 Architectural Model NWC | FS1018-CPM-ZZ-ZZ-M-A-0003
FS1018-CPM-ZZ-ZZ-M-A-0004 | Architectural Model IFC | P25 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-16 |  | TRUE | FS1018-CPM-ZZ-ZZ-M-A-0004 Architectural Model IFC | FS1018-CPM-ZZ-ZZ-M-A-0004
FS1018-CPM-ZZ-ZZ-M-A-0005 | Architectural Model Revit | P25 | Completed | 2025-04-09 | DFE Review | A - Accepted | 2025-04-16 |  | TRUE | FS1018-CPM-ZZ-ZZ-M-A-0005 Architectural Model Revit | FS1018-CPM-ZZ-ZZ-M-A-0005
FS1018-CPM-ZZ-ZZ-V-A-0001 | External Flythrough Video | P01 | Completed | 2025-03-14 | DFE Review | A - Accepted | 2025-04-03 | no comments | TRUE | FS1018-CPM-ZZ-ZZ-V-A-0001 External Flythrough Video | FS1018-CPM-ZZ-ZZ-V-A-0001
FS1018-CPM-ZZ-ZZ-V-A-0002 | Internal Flythrough Video | P01 | In Progress | 2025-03-14 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Various comments picked up elsewhere in the drawings pack. For example, hall lighting clashes with clear height requirements, odd pushplates to some doors, some pinboards clashing with dado trunking, ceiling rafts clashing with ceiling grid. | TRUE | FS1018-CPM-ZZ-ZZ-V-A-0002 Internal Flythrough Video | FS1018-CPM-ZZ-ZZ-V-A-0002
FS1018-CPM-ZZ-ZZ-V-A-0002 | Internal Flythrough Video | P01 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-CPM-ZZ-ZZ-V-A-0002 Internal Flythrough Video | FS1018-CPM-ZZ-ZZ-V-A-0002
FS1018-EVR-XX-XX-D-O-0001 | Server Room Location | P03 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-EVR-XX-XX-D-O-0001 Server Room Location | FS1018-EVR-XX-XX-D-O-0001
FS1018-EVR-XX-XX-D-O-0002 | ICT Plans | P03 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-EVR-XX-XX-D-O-0002 ICT Plans | FS1018-EVR-XX-XX-D-O-0002
FS1018-EVR-XX-XX-D-O-0003 | Wireless Heat Maps | P01 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-EVR-XX-XX-D-O-0003 Wireless Heat Maps | FS1018-EVR-XX-XX-D-O-0003
FS1018-EVR-XX-XX-D-O-0004 | Server Cabinet Layout | P01 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-EVR-XX-XX-D-O-0004 Server Cabinet Layout | FS1018-EVR-XX-XX-D-O-0004
FS1018-EVR-XX-XX-G-O-0001 | ICT Network Diagrams | P02 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-EVR-XX-XX-G-O-0001 ICT Network Diagrams | FS1018-EVR-XX-XX-G-O-0001
FS1018-EVR-XX-XX-L-O-0001 | ICT Equipment List | P02 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-EVR-XX-XX-L-O-0001 ICT Equipment List | FS1018-EVR-XX-XX-L-O-0001
FS1018-EVR-XX-XX-L-O-0002 | ICT Cost Matrix | P02 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-EVR-XX-XX-L-O-0002 ICT Cost Matrix | FS1018-EVR-XX-XX-L-O-0002
FS1018-EVR-XX-XX-L-O-0003 | ICT Small Power and Data Schedule | P01 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-EVR-XX-XX-L-O-0003 ICT Small Power and Data Schedule | FS1018-EVR-XX-XX-L-O-0003
FS1018-EVR-XX-XX-L-O-0004 | ICT Construction Programme | P02 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-EVR-XX-XX-L-O-0004 ICT Construction Programme | FS1018-EVR-XX-XX-L-O-0004
FS1018-EVR-XX-XX-T-O-0002 | ICT Calculations | P01 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-EVR-XX-XX-T-O-0002 ICT Calculations | FS1018-EVR-XX-XX-T-O-0002
FS1018-EVR-XX-XX-T-O-0004 | ICT Contractor's Proposals | P01 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-EVR-XX-XX-T-O-0004 ICT Contractor's Proposals | FS1018-EVR-XX-XX-T-O-0004
FS1018-EVR-XX-XX-T-O-0005 | Post Award ICT Meetings (PAM) Agendas | P01 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-EVR-XX-XX-T-O-0005 Post Award ICT Meetings (PAM) Agendas | FS1018-EVR-XX-XX-T-O-0005
FS1018-EVR-XX-XX-T-O-0006 | User Acceptance Testing (UAT) Schedule | P01 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-EVR-XX-XX-T-O-0006 User Acceptance Testing (UAT) Schedule | FS1018-EVR-XX-XX-T-O-0006
FS1018-EVR-XX-XX-T-O-0007 | Post Award ICT Meetings (PAM) Minutes | P01 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-EVR-XX-XX-T-O-0007 Post Award ICT Meetings (PAM) Minutes | FS1018-EVR-XX-XX-T-O-0007
FS1018-HBC-XX-XX-D-X-0001 | Site Construction Plan | P01 | In Progress | 2025-03-26 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-D-X-0001 Site Construction Plan | FS1018-HBC-XX-XX-D-X-0001
FS1018-HBC-XX-XX-D-X-0003 | Site Set Up Plan Phase 1 | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-19 | this document shows the correct car park layouts for this phase. therefore can FS1018-HBC-XX-XX-D-X-0001 be removed? | TRUE | FS1018-HBC-XX-XX-D-X-0003 Site Set Up Plan Phase 1 | FS1018-HBC-XX-XX-D-X-0003
FS1018-HBC-XX-XX-D-X-0003 | Site Set Up Plan Phase 1 | P02 | In Progress | 2025-03-26 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-D-X-0003 Site Set Up Plan Phase 1 | FS1018-HBC-XX-XX-D-X-0003
FS1018-HBC-XX-XX-D-X-0004 | Site Set Up Plan Phase 2 Section 1 | P02 | In Progress | 2025-03-26 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-D-X-0004 Site Set Up Plan Phase 2 Section 1 | FS1018-HBC-XX-XX-D-X-0004
FS1018-HBC-XX-XX-D-X-0005 | Site Set Up Plan Phase 2 Section 2 | P01 | In Progress | 2025-03-26 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-D-X-0005 Site Set Up Plan Phase 2 Section 2 | FS1018-HBC-XX-XX-D-X-0005
FS1018-HBC-XX-XX-D-X-0006 | Site Set Up Plan Phase 3 | P01 | In Progress | 2025-03-26 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-D-X-0006 Site Set Up Plan Phase 3 | FS1018-HBC-XX-XX-D-X-0006
FS1018-HBC-XX-XX-L-X-0001 | MIDP | P15 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-L-X-0001 MIDP | FS1018-HBC-XX-XX-L-X-0001
FS1018-HBC-XX-XX-L-X-0003 | Design Programme | P02 | In Progress | 2025-03-26 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-L-X-0003 Design Programme | FS1018-HBC-XX-XX-L-X-0003
FS1018-HBC-XX-XX-L-X-0004 | Construction Programme | P02 | In Progress | 2025-03-26 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-L-X-0004 Construction Programme | FS1018-HBC-XX-XX-L-X-0004
FS1018-HBC-XX-XX-L-X-0005 | Master Programme | P02 | In Progress | 2025-03-26 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-L-X-0005 Master Programme | FS1018-HBC-XX-XX-L-X-0005
FS1018-HBC-XX-XX-L-X-0006 | Works Package Procurement Programme | P02 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-L-X-0006 Works Package Procurement Programme | FS1018-HBC-XX-XX-L-X-0006
FS1018-HBC-XX-XX-L-X-0007 | Risk Register | P02 | In Progress | 2025-03-26 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-L-X-0007 Risk Register | FS1018-HBC-XX-XX-L-X-0007
FS1018-HBC-XX-XX-L-X-0008 | PCSA | P02 | Completed | 2025-03-28 | DFE Review | A - Accepted | 2025-04-01 |  | TRUE | FS1018-HBC-XX-XX-L-X-0008 PCSA | FS1018-HBC-XX-XX-L-X-0008
FS1018-HBC-XX-XX-L-X-0009 | PCSA Milestone Schedule | P02 | Completed | 2025-03-28 | DFE Review | A - Accepted | 2025-04-01 | Standard milestone PCSA payment schedule. | TRUE | FS1018-HBC-XX-XX-L-X-0009 PCSA Milestone Schedule | FS1018-HBC-XX-XX-L-X-0009
FS1018-HBC-XX-XX-L-X-0010 | PCSA Certificate Of Completion | P02 | Completed | 2025-03-28 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-HBC-XX-XX-L-X-0010 PCSA Certificate Of Completion | FS1018-HBC-XX-XX-L-X-0010
FS1018-HBC-XX-XX-L-X-0011 | Cashflow Forecast | P02 | Completed | 2025-04-01 | DFE Review | A - Accepted | 2025-04-01 | Construction cashflow included. | TRUE | FS1018-HBC-XX-XX-L-X-0011 Cashflow Forecast | FS1018-HBC-XX-XX-L-X-0011
FS1018-HBC-XX-XX-L-X-0012 | Framework Pricing Schedule | P03 | Completed | 2025-03-28 | DFE Review | C - Rejected | 2025-03-31 | A1 Cost summary sheet. The sums entered do not match nor total correctly. The whole schedule needs to be reviewed by contractor and QA correctly. | FALSE | FS1018-HBC-XX-XX-L-X-0012 Framework Pricing Schedule | FS1018-HBC-XX-XX-L-X-0012
FS1018-HBC-XX-XX-L-X-0012 | Framework Pricing Schedule | P03 | Completed | 2025-04-10 | DFE Review of Responses | C - Rejected | 2025-04-10 |  | FALSE | FS1018-HBC-XX-XX-L-X-0012 Framework Pricing Schedule | FS1018-HBC-XX-XX-L-X-0012
FS1018-HBC-XX-XX-L-X-0012 | Framework Pricing Schedule | P04 | In Progress | 2025-04-10 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-L-X-0012 Framework Pricing Schedule | FS1018-HBC-XX-XX-L-X-0012
FS1018-HBC-XX-XX-L-X-0013 | DFE KPIs | P02 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-L-X-0013 DFE KPIs | FS1018-HBC-XX-XX-L-X-0013
FS1018-HBC-XX-XX-L-X-0014 | Supplier Directory CV | P03 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-L-X-0014 Supplier Directory CV | FS1018-HBC-XX-XX-L-X-0014
FS1018-HBC-XX-XX-L-X-0016 | Handover Training Plan | P02 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-L-X-0016 Handover Training Plan | FS1018-HBC-XX-XX-L-X-0016
FS1018-HBC-XX-XX-L-X-0018 | HB Social Value KPIs | P02 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-L-X-0018 HB Social Value KPIs | FS1018-HBC-XX-XX-L-X-0018
FS1018-HBC-XX-XX-L-X-0019 | Site Organisation Chart | P01 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-L-X-0019 Site Organisation Chart | FS1018-HBC-XX-XX-L-X-0019
FS1018-HBC-XX-XX-L-X-0020 | Commissioning Programme | P01 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-L-X-0020 Commissioning Programme | FS1018-HBC-XX-XX-L-X-0020
FS1018-HBC-XX-XX-L-X-1001 | Quality Management Plan | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 |  | TRUE | FS1018-HBC-XX-XX-L-X-1001 Quality Management Plan | FS1018-HBC-XX-XX-L-X-1001
FS1018-HBC-XX-XX-L-X-1002 | Sustainable Estate Strategy | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | Details need updating throughout to reflect current design proposal. | TRUE | FS1018-HBC-XX-XX-L-X-1002 Sustainable Estate Strategy | FS1018-HBC-XX-XX-L-X-1002
FS1018-HBC-XX-XX-L-X-1002 | Sustainable Estate Strategy | P03 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-HBC-XX-XX-L-X-1002 Sustainable Estate Strategy | FS1018-HBC-XX-XX-L-X-1002
FS1018-HBC-XX-XX-L-X-1003 | Lift Specification | P01 | In Progress | 2025-03-26 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-L-X-1003 Lift Specification | FS1018-HBC-XX-XX-L-X-1003
FS1018-HBC-XX-XX-L-X-1004 | Project Execution Plan | P02 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-L-X-1004 Project Execution Plan | FS1018-HBC-XX-XX-L-X-1004
FS1018-HBC-XX-XX-L-X-3000 | Derogations Schedule | P05 | In Progress | 2025-04-17 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-L-X-3000 Derogations Schedule | FS1018-HBC-XX-XX-L-X-3000
FS1018-HBC-XX-XX-L-X-4000 | Planning Condition Tracker | P01 | In Progress | 2025-03-26 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-L-X-4000 Planning Condition Tracker | FS1018-HBC-XX-XX-L-X-4000
FS1018-HBC-XX-XX-T-X-0001 | Construction Phasing Plan | P03 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-T-X-0001 Construction Phasing Plan | FS1018-HBC-XX-XX-T-X-0001
FS1018-HBC-XX-XX-T-X-0012 | Cost Plan Summary | P01 | In Progress | 2025-04-10 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-T-X-0012 Cost Plan Summary | FS1018-HBC-XX-XX-T-X-0012
FS1018-HBC-XX-XX-T-X-0024 | CEM7 Meeting Minutes | P01 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 |  | TRUE | FS1018-HBC-XX-XX-T-X-0024 CEM7 Meeting Minutes | FS1018-HBC-XX-XX-T-X-0024
FS1018-HBC-XX-XX-T-X-0025 | CEM8 Meeting Minutes | P01 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 |  | TRUE | FS1018-HBC-XX-XX-T-X-0025 CEM8 Meeting Minutes | FS1018-HBC-XX-XX-T-X-0025
FS1018-HBC-XX-XX-T-X-0026 | CEM8-9A Meeting Minutes | P01 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 |  | TRUE | FS1018-HBC-XX-XX-T-X-0026 CEM8-9A Meeting Minutes | FS1018-HBC-XX-XX-T-X-0026
FS1018-HBC-XX-XX-T-X-0027 | CEM09 Meeting Minutes | P01 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 |  | TRUE | FS1018-HBC-XX-XX-T-X-0027 CEM09 Meeting Minutes | FS1018-HBC-XX-XX-T-X-0027
FS1018-HBC-XX-XX-T-X-0028 | CEM10 Meeting Minutes | P01 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 |  | TRUE | FS1018-HBC-XX-XX-T-X-0028 CEM10 Meeting Minutes | FS1018-HBC-XX-XX-T-X-0028
FS1018-HBC-XX-XX-T-X-0029 | CEM10A Meeting Minutes | P01 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 |  | TRUE | FS1018-HBC-XX-XX-T-X-0029 CEM10A Meeting Minutes | FS1018-HBC-XX-XX-T-X-0029
FS1018-HBC-XX-XX-T-X-0030 | CEM11 Meeting Minutes | P01 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 |  | TRUE | FS1018-HBC-XX-XX-T-X-0030 CEM11 Meeting Minutes | FS1018-HBC-XX-XX-T-X-0030
FS1018-HBC-XX-XX-T-X-0031 | CEM12 Meeting Minutes | P01 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 |  | TRUE | FS1018-HBC-XX-XX-T-X-0031 CEM12 Meeting Minutes | FS1018-HBC-XX-XX-T-X-0031
FS1018-HBC-XX-XX-T-X-0033 | CEM07 Agenda | P01 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 |  | TRUE | FS1018-HBC-XX-XX-T-X-0033 CEM07 Agenda | FS1018-HBC-XX-XX-T-X-0033
FS1018-HBC-XX-XX-T-X-0034 | CEM08 Agenda | P01 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 |  | TRUE | FS1018-HBC-XX-XX-T-X-0034 CEM08 Agenda | FS1018-HBC-XX-XX-T-X-0034
FS1018-HBC-XX-XX-T-X-0035 | CEM09 Agenda | P01 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 |  | TRUE | FS1018-HBC-XX-XX-T-X-0035 CEM09 Agenda | FS1018-HBC-XX-XX-T-X-0035
FS1018-HBC-XX-XX-T-X-0036 | CEM08-9A Agenda | P01 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 |  | TRUE | FS1018-HBC-XX-XX-T-X-0036 CEM08-9A Agenda | FS1018-HBC-XX-XX-T-X-0036
FS1018-HBC-XX-XX-T-X-0037 | CEM10 Meeting Agenda | P01 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 |  | TRUE | FS1018-HBC-XX-XX-T-X-0037 CEM10 Meeting Agenda | FS1018-HBC-XX-XX-T-X-0037
FS1018-HBC-XX-XX-T-X-0038 | CEM10A Agenda | P01 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 |  | TRUE | FS1018-HBC-XX-XX-T-X-0038 CEM10A Agenda | FS1018-HBC-XX-XX-T-X-0038
FS1018-HBC-XX-XX-T-X-0039 | CEM11 Agenda | P01 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 |  | TRUE | FS1018-HBC-XX-XX-T-X-0039 CEM11 Agenda | FS1018-HBC-XX-XX-T-X-0039
FS1018-HBC-XX-XX-T-X-0040 | CEM12 Agenda | P01 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 |  | TRUE | FS1018-HBC-XX-XX-T-X-0040 CEM12 Agenda | FS1018-HBC-XX-XX-T-X-0040
FS1018-HBC-XX-XX-T-X-0042 | Employer Necessary Consents | P01 | In Progress | 2025-03-26 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-T-X-0042 Employer Necessary Consents | FS1018-HBC-XX-XX-T-X-0042
FS1018-HBC-XX-XX-T-X-0043 | Construction Method Statement | P01 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-T-X-0043 Construction Method Statement | FS1018-HBC-XX-XX-T-X-0043
FS1018-HBC-XX-XX-T-X-0044 | Handover Strategy | P01 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-HBC-XX-XX-T-X-0044 Handover Strategy | FS1018-HBC-XX-XX-T-X-0044
FS1018-HBC-XX-XX-T-X-0045 | Thermal Assessment | P01 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-01 |  | TRUE | FS1018-HBC-XX-XX-T-X-0045 Thermal Assessment | FS1018-HBC-XX-XX-T-X-0045
FS1018-HEX-XX-XX-T-C-0004 | Civil Design Philosophy | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-25 | D1 3. Geo-Environmental notes groundwater risk - drainage design is sealed/lined to prevent groundwater ingress and will not therefore not reduce groundwater around the structure. Geotechnical input required. D2 4. No flooding information provided as part of this submission - condition, water levels within watercourse, overland flow routes. Risk of back flow when water level in culvert is high. D3. 5. Status of Internal Drainage Board (IDB) approval to be confirmed as it will affect the design requirements. D4 5. Works are proposed within 9m of the watercourse culvert. Constructability risk that will need to be managed and agreed with IDB - Foundation and drainage installation. Pre and post construction survey of the culvert may be necessary D5 5. It has been noted that additional survey is required to determine existing drains, condition and levels. At this stage we would expect survey works to be complete especially for location and levels of outfalls. D6 6. It has been noted that additional design may be necessary following engagement with IDB and flow rates are yet to be agreed. Therefore the Stage 4 Technical Design is not complete. D7 6. Specialist manufacturer design is still required for storage tanks. Proposed tank depth does not reflect manufacturer storage units, shallow depth of cover, flotation risk and proximity to structure are all risks to be managed within the storage tank design. D8 7. Foul design is yet to be agreed with Anglian Water, location and levels to be confirmed D9 9. Has a timeline for outstanding surveys, design and approvals been agreed? Extent of survey, repairs to existing network, specialist design, conditions/redesign are significant risks. D10 Information available does not include: hydraulic analysis results treatment strategy Emergy shutoff and containment in the eventof a fire ot pollution event to protect downstream watercourse. profiles connection details specialist design elements - linear drains, storage tank | TRUE | FS1018-HEX-XX-XX-T-C-0004 Civil Design Philosophy | FS1018-HEX-XX-XX-T-C-0004
FS1018-HEX-XX-XX-T-C-0004 | Civil Design Philosophy | P02 | In Progress | 2025-03-25 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-XX-XX-T-C-0004 Civil Design Philosophy | FS1018-HEX-XX-XX-T-C-0004
FS1018-HEX-XX-XX-T-C-0010 | Risk Register | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-25 | Consider adding approvals, additional requirements from IDB, surcharged outfall, pollution control/emergency shutoff and remaining design/reliance on specialist designers | TRUE | FS1018-HEX-XX-XX-T-C-0010 Risk Register | FS1018-HEX-XX-XX-T-C-0010
FS1018-HEX-XX-XX-T-C-0010 | Risk Register | P03 | In Progress | 2025-03-25 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-XX-XX-T-C-0010 Risk Register | FS1018-HEX-XX-XX-T-C-0010
FS1018-HEX-XX-XX-T-C-0011 | Drainage Specification | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-25 | 1. Geotextile and geomembrane specification requirements and testing to be confirmed. 2. Confirm if non-return and emergency shutoff valves are required. 3. Confirm any specialist drainage signage required. 4. Specialist design requirements may need to be included when available. | TRUE | FS1018-HEX-XX-XX-T-C-0011 Drainage Specification | FS1018-HEX-XX-XX-T-C-0011
FS1018-HEX-XX-XX-T-C-0011 | Drainage Specification | P01 | In Progress | 2025-03-25 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-XX-XX-T-C-0011 Drainage Specification | FS1018-HEX-XX-XX-T-C-0011
FS1018-HEX-XX-XX-T-C-0012 | Earthworks Specification | P01 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-HEX-XX-XX-T-C-0012 Earthworks Specification | FS1018-HEX-XX-XX-T-C-0012
FS1018-HEX-XX-XX-T-H-0001 | Transport Assessment | P02 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-HEX-XX-XX-T-H-0001 Transport Assessment | FS1018-HEX-XX-XX-T-H-0001
FS1018-HEX-XX-XX-T-S-0003 | Structural Design Philosophy | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Please refer to comments at the end of the uploaded file. | TRUE | FS1018-HEX-XX-XX-T-S-0003 Structural Design Philosophy | FS1018-HEX-XX-XX-T-S-0003
FS1018-HEX-XX-XX-T-S-0003 | Structural Design Philosophy | P02 | In Progress | 2025-03-28 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-XX-XX-T-S-0003 Structural Design Philosophy | FS1018-HEX-XX-XX-T-S-0003
FS1018-HEX-XX-XX-T-S-0004 | Concrete Specification | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Please review in light of other comments. | TRUE | FS1018-HEX-XX-XX-T-S-0004 Concrete Specification | FS1018-HEX-XX-XX-T-S-0004
FS1018-HEX-XX-XX-T-S-0004 | Concrete Specification | P01 | In Progress | 2025-03-28 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-XX-XX-T-S-0004 Concrete Specification | FS1018-HEX-XX-XX-T-S-0004
FS1018-HEX-XX-XX-T-S-0005 | Steelwork Specification | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 |  | TRUE | FS1018-HEX-XX-XX-T-S-0005 Steelwork Specification | FS1018-HEX-XX-XX-T-S-0005
FS1018-HEX-XX-XX-T-S-0005 | Steelwork Specification | P01 | In Progress | 2025-03-28 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-XX-XX-T-S-0005 Steelwork Specification | FS1018-HEX-XX-XX-T-S-0005
FS1018-HEX-XX-XX-T-S-0006 | Piling Specification | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Please review in light of other comments. | TRUE | FS1018-HEX-XX-XX-T-S-0006 Piling Specification | FS1018-HEX-XX-XX-T-S-0006
FS1018-HEX-XX-XX-T-S-0006 | Piling Specification | P01 | In Progress | 2025-03-28 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-XX-XX-T-S-0006 Piling Specification | FS1018-HEX-XX-XX-T-S-0006
FS1018-HEX-ZZ-00-D-S-0101 | Foundation Layout | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 |  | TRUE | FS1018-HEX-ZZ-00-D-S-0101 Foundation Layout | FS1018-HEX-ZZ-00-D-S-0101
FS1018-HEX-ZZ-00-D-S-0101 | Foundation Layout | P03 | In Progress | 2025-03-28 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-ZZ-00-D-S-0101 Foundation Layout | FS1018-HEX-ZZ-00-D-S-0101
FS1018-HEX-ZZ-00-D-S-0102 | Foundation Details | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 |  | TRUE | FS1018-HEX-ZZ-00-D-S-0102 Foundation Details | FS1018-HEX-ZZ-00-D-S-0102
FS1018-HEX-ZZ-00-D-S-0102 | Foundation Details | P01 | In Progress | 2025-03-28 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-ZZ-00-D-S-0102 Foundation Details | FS1018-HEX-ZZ-00-D-S-0102
FS1018-HEX-ZZ-00-D-S-0200 | Ground Floor Column Plan | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Typical design intent for column base plates/ HD arrangement must be shown in section and plan for each column type and for columns at the separation joint. Some beam levels in staircase still to be confirmed. Overall lateral stability strategy is not clear qualitatively. Lost of bracing is concentrated in the sports hall but very few braced bays in the main building. Vertical braces not doubled up along the separation joint on GL - D1/E. In the sports hall there is a significant amount of glazed elevation but no bracing - are any connections that are intended to be moment resisting? | TRUE | FS1018-HEX-ZZ-00-D-S-0200 Ground Floor Column Plan | FS1018-HEX-ZZ-00-D-S-0200
FS1018-HEX-ZZ-00-D-S-0200 | Ground Floor Column Plan | P03 | In Progress | 2025-03-28 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-ZZ-00-D-S-0200 Ground Floor Column Plan | FS1018-HEX-ZZ-00-D-S-0200
FS1018-HEX-ZZ-01-D-S-0201 | First Floor Steelwork Layout | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Please review in light of other comments, particularly overall stability/bracing, separation joints/ movement joints etc. Is there an intention for a separation joint along GL - S? | TRUE | FS1018-HEX-ZZ-01-D-S-0201 First Floor Steelwork Layout | FS1018-HEX-ZZ-01-D-S-0201
FS1018-HEX-ZZ-01-D-S-0201 | First Floor Steelwork Layout | P03 | In Progress | 2025-03-28 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-ZZ-01-D-S-0201 First Floor Steelwork Layout | FS1018-HEX-ZZ-01-D-S-0201
FS1018-HEX-ZZ-02-D-S-0202 | Second Floor Steelwork Layout | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Please review in light of other comments, particularly overall stability/bracing, separation joints/ movement joints etc. Is there an intention for a separation joint along GL - S? | TRUE | FS1018-HEX-ZZ-02-D-S-0202 Second Floor Steelwork Layout | FS1018-HEX-ZZ-02-D-S-0202
FS1018-HEX-ZZ-02-D-S-0202 | Second Floor Steelwork Layout | P03 | In Progress | 2025-03-28 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-ZZ-02-D-S-0202 Second Floor Steelwork Layout | FS1018-HEX-ZZ-02-D-S-0202
FS1018-HEX-ZZ-RF-D-S-0203 | Main Roof Steelwork Layout | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Please review in light of other comments, particularly overall stability/bracing, separation joints/ movement joints etc. Is there an intention for a separation joint along GL - S? | TRUE | FS1018-HEX-ZZ-RF-D-S-0203 Main Roof Steelwork Layout | FS1018-HEX-ZZ-RF-D-S-0203
FS1018-HEX-ZZ-RF-D-S-0203 | Main Roof Steelwork Layout | P03 | In Progress | 2025-03-28 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-ZZ-RF-D-S-0203 Main Roof Steelwork Layout | FS1018-HEX-ZZ-RF-D-S-0203
FS1018-HEX-ZZ-RF-D-S-0204 | Hall Roof Steelwork Layouts | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Please review in light of other comments, particularly overall stability/bracing, separation joints/ movement joints etc. Is there an intention for a separation joint along GL - S? | TRUE | FS1018-HEX-ZZ-RF-D-S-0204 Hall Roof Steelwork Layouts | FS1018-HEX-ZZ-RF-D-S-0204
FS1018-HEX-ZZ-RF-D-S-0204 | Hall Roof Steelwork Layouts | P03 | In Progress | 2025-03-28 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-ZZ-RF-D-S-0204 Hall Roof Steelwork Layouts | FS1018-HEX-ZZ-RF-D-S-0204
FS1018-HEX-ZZ-RF-D-S-0205 | Parapet Steelwork Layout | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Please review in light of other comments. | TRUE | FS1018-HEX-ZZ-RF-D-S-0205 Parapet Steelwork Layout | FS1018-HEX-ZZ-RF-D-S-0205
FS1018-HEX-ZZ-RF-D-S-0205 | Parapet Steelwork Layout | P03 | In Progress | 2025-03-28 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-ZZ-RF-D-S-0205 Parapet Steelwork Layout | FS1018-HEX-ZZ-RF-D-S-0205
FS1018-HEX-ZZ-XX-D-S-0001 | Project Notes | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Piling Notes - Reference to precast piles? Piling Notes - Piling Specification appears incomplete - Provide a full Project Specification covering all relevant aspects from Section B1 of ICESPERW Piling Notes - Is 500mm anchorage sufficient? What bar diameter is this to be? Structural Steelwork Notes - Project Specification should be reviewed against NSSS Section Checklists and all relevant items included. Structural Steelwork Notes - Connection loads not available Structural Masonry Notes - typical indicative details for masonry should be included on drawings to supplement these notes. | TRUE | FS1018-HEX-ZZ-XX-D-S-0001 Project Notes | FS1018-HEX-ZZ-XX-D-S-0001
FS1018-HEX-ZZ-XX-D-S-0001 | Project Notes | P02 | In Progress | 2025-03-28 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-ZZ-XX-D-S-0001 Project Notes | FS1018-HEX-ZZ-XX-D-S-0001
FS1018-HEX-ZZ-ZZ-D-C-5200 | Surface Water Drainage Layout Sheet 1 | P05 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-25 | 1. Due to the size and shape of tank there is a risk of ponding within the tank. Designer and Manufacturer to consider fall across the tank so it can drain out. 2. Tank Depth of cover = 0.73 could be difficult to get a manufacturers design as they generally specify 0.9 - 1.2m minimum. 3. clash and constructability risk between building and storage tank 4. Potential constructibility risks within and adjacent to IDB maintenance strip to be considered - piling, drainage, plant movement, vibration and loading adjacent to culvert 5. Outfall connection - Confirm downstream pipe size, may require access point (SSG) rather than a saddle connection to existing. 6. As surface water drainage is sealed to prevent ingress from groundwater. Can we confirm that this has been communicated and taken into account for the structure design. Geotech and Structures to confirm. 7. Acute angle <90deg between incoming and outgoing pipes. 8. Terminology could be confusing - is Private proposed or an existing asset belonging to others? | TRUE | FS1018-HEX-ZZ-ZZ-D-C-5200 Surface Water Drainage Layout Sheet 1 | FS1018-HEX-ZZ-ZZ-D-C-5200
FS1018-HEX-ZZ-ZZ-D-C-5200 | Surface Water Drainage Layout Sheet 1 | P05 | In Progress | 2025-03-25 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-ZZ-ZZ-D-C-5200 Surface Water Drainage Layout Sheet 1 | FS1018-HEX-ZZ-ZZ-D-C-5200
FS1018-HEX-ZZ-ZZ-D-C-5201 | Surface Water Drainage Layout Sheet 2 | P05 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-25 | See comments for sheet FS1018-HEX-ZZ-ZZ-D-C-5200 | TRUE | FS1018-HEX-ZZ-ZZ-D-C-5201 Surface Water Drainage Layout Sheet 2 | FS1018-HEX-ZZ-ZZ-D-C-5201
FS1018-HEX-ZZ-ZZ-D-C-5201 | Surface Water Drainage Layout Sheet 2 | P05 | In Progress | 2025-03-25 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-ZZ-ZZ-D-C-5201 Surface Water Drainage Layout Sheet 2 | FS1018-HEX-ZZ-ZZ-D-C-5201
FS1018-HEX-ZZ-ZZ-D-C-5205 | Foul Water Drainage Layout | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-25 | 1. Depth, size and gradient of underfloor pipes to be confirmed to ensure there is no clash with foundation and chamber connections can be achieved. Groundwater risk to pipe connections 2. Gully connection to FW1a has shallow cover which may affect performance and constructability 3. Outfall location, levels and condition will need to be confirmed to prove connection. 4. Legend - Existing SW sewer linetype scale is not clear. 5. Terminology could be confusing - is Private proposed or an existing asset belonging to others? | TRUE | FS1018-HEX-ZZ-ZZ-D-C-5205 Foul Water Drainage Layout | FS1018-HEX-ZZ-ZZ-D-C-5205
FS1018-HEX-ZZ-ZZ-D-C-5205 | Foul Water Drainage Layout | P04 | In Progress | 2025-03-25 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-ZZ-ZZ-D-C-5205 Foul Water Drainage Layout | FS1018-HEX-ZZ-ZZ-D-C-5205
FS1018-HEX-ZZ-ZZ-D-C-5210 | Drainage Construction Details Sheet 1 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-25 | 1. Details refer to SFA 7th Edition rather than SSG. 2. orifice plate - size, material, thickness and connection requirements required. 3. text missing from orifice chamber detail. 4. wrapping filter drains with impermeable membrane will prevent water in/out. if the aim is to prevent ingress/infiltration then it should state 'trench to be lined with impermeable membrane to prevent ingress of groundwater'. 5. Extent of geotextile is not clear. Geotextile will be required between sand and aggregate. 6. Surface water plans appear to show dry swales (TBC) A detail will be required. | TRUE | FS1018-HEX-ZZ-ZZ-D-C-5210 Drainage Construction Details Sheet 1 | FS1018-HEX-ZZ-ZZ-D-C-5210
FS1018-HEX-ZZ-ZZ-D-C-5210 | Drainage Construction Details Sheet 1 | P03 | In Progress | 2025-03-25 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-ZZ-ZZ-D-C-5210 Drainage Construction Details Sheet 1 | FS1018-HEX-ZZ-ZZ-D-C-5210
FS1018-HEX-ZZ-ZZ-D-C-5211 | Drainage Construction Details Sheet 2 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-25 | 1. storage crate units are typically 400 - 500mm high which doesn't fit with 0.74m depth of tank. 2. Catchpit - Additional details required: Brick, mortar, steps. Are weep pipes proposed for draining lower trench bedding? 3. Swale comments: Swale side slope should be shown as 1:3 Max. A dry swale detail is required? Is there a max water depth, freeboard or base width? Longitudinal slopes TBC Liner and geotextile not clear due to line thickness, scale and adjacent hatching. 4. Additional details may be required such as rodding eye, RWP connection, linear drain outlet and siphonic break chamber. | TRUE | FS1018-HEX-ZZ-ZZ-D-C-5211 Drainage Construction Details Sheet 2 | FS1018-HEX-ZZ-ZZ-D-C-5211
FS1018-HEX-ZZ-ZZ-D-C-5211 | Drainage Construction Details Sheet 2 | P03 | In Progress | 2025-03-25 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-ZZ-ZZ-D-C-5211 Drainage Construction Details Sheet 2 | FS1018-HEX-ZZ-ZZ-D-C-5211
FS1018-HEX-ZZ-ZZ-D-C-9000 | Earthworks Analysis | P01 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-HEX-ZZ-ZZ-D-C-9000 Earthworks Analysis | FS1018-HEX-ZZ-ZZ-D-C-9000
FS1018-HEX-ZZ-ZZ-D-C-9020 | External Works Layout Sheet 1 | P02 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-HEX-ZZ-ZZ-D-C-9020 External Works Layout Sheet 1 | FS1018-HEX-ZZ-ZZ-D-C-9020
FS1018-HEX-ZZ-ZZ-D-C-9021 | External Works Layout Sheet 2 | P02 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-HEX-ZZ-ZZ-D-C-9021 External Works Layout Sheet 2 | FS1018-HEX-ZZ-ZZ-D-C-9021
FS1018-HEX-ZZ-ZZ-D-C-9025 | External Works Construction Details | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-25 | Permeable block paving - consider nominal fall across geomembrane to ensure water doesn't become perched. | TRUE | FS1018-HEX-ZZ-ZZ-D-C-9025 External Works Construction Details | FS1018-HEX-ZZ-ZZ-D-C-9025
FS1018-HEX-ZZ-ZZ-D-C-9025 | External Works Construction Details | P02 | In Progress | 2025-03-25 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-ZZ-ZZ-D-C-9025 External Works Construction Details | FS1018-HEX-ZZ-ZZ-D-C-9025
FS1018-HEX-ZZ-ZZ-D-S-0501 | Building Elevations Sheet 01 Of 02 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Please review in light of other comments, particularly overall stability/bracing, separation joints/ movement joints etc. Is there an intention for a separation joint along GL - S? | TRUE | FS1018-HEX-ZZ-ZZ-D-S-0501 Building Elevations Sheet 01 Of 02 | FS1018-HEX-ZZ-ZZ-D-S-0501
FS1018-HEX-ZZ-ZZ-D-S-0501 | Building Elevations Sheet 01 Of 02 | P03 | In Progress | 2025-03-28 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-ZZ-ZZ-D-S-0501 Building Elevations Sheet 01 Of 02 | FS1018-HEX-ZZ-ZZ-D-S-0501
FS1018-HEX-ZZ-ZZ-D-S-0502 | Building Elevations Sheet 02 Of 02 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Please review in light of other comments, particularly overall stability/bracing, separation joints/ movement joints etc. Is there an intention for a separation joint along GL - S? | TRUE | FS1018-HEX-ZZ-ZZ-D-S-0502 Building Elevations Sheet 02 Of 02 | FS1018-HEX-ZZ-ZZ-D-S-0502
FS1018-HEX-ZZ-ZZ-D-S-0502 | Building Elevations Sheet 02 Of 02 | P03 | In Progress | 2025-03-28 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-ZZ-ZZ-D-S-0502 Building Elevations Sheet 02 Of 02 | FS1018-HEX-ZZ-ZZ-D-S-0502
FS1018-HEX-ZZ-ZZ-D-S-0503 | Bracing Elevations | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Please review in light of other comments, particularly overall stability/bracing, separation joints/ movement joints etc. Is there an intention for a separation joint along GL - S? | TRUE | FS1018-HEX-ZZ-ZZ-D-S-0503 Bracing Elevations | FS1018-HEX-ZZ-ZZ-D-S-0503
FS1018-HEX-ZZ-ZZ-D-S-0503 | Bracing Elevations | P03 | In Progress | 2025-03-28 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-ZZ-ZZ-D-S-0503 Bracing Elevations | FS1018-HEX-ZZ-ZZ-D-S-0503
FS1018-HEX-ZZ-ZZ-D-S-0601 | Building Sections | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Detail of roof build-up and framing of roof lights and vents not available. Some vertical members shown in blue on Section - 3-3, what are these? Does the main roof rafter not need any stays/restraints in uplift? No details available. | TRUE | FS1018-HEX-ZZ-ZZ-D-S-0601 Building Sections | FS1018-HEX-ZZ-ZZ-D-S-0601
FS1018-HEX-ZZ-ZZ-D-S-0601 | Building Sections | P03 | In Progress | 2025-03-28 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-ZZ-ZZ-D-S-0601 Building Sections | FS1018-HEX-ZZ-ZZ-D-S-0601
FS1018-HEX-ZZ-ZZ-D-S-0602 | Structural Sections and Details | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Please review in light of other comments, particularly overall stability/bracing, separation joints/ movement joints etc. Is there an intention for a separation joint along GL - S? Tying of hollow core to steelwork - can 4x slots be formed in a 200 the hollo core slab? The bearing of hollow core slab on beams appears small - confirm bearing length. Due to chamfer of hollo core slabs has the potential of hollow core shearing off been considered in the temporary stage? No detail for precast staircase foundation and its connection. No details of any barriers/handrails etc. Design intent of masonry supports/curtain walling not clear with the details presented. Notes re Co-ordination TBC should be removed at this stage. Tall parapets - no connection intent detail available. What type of connections are intended generally - no details available. Detail through riser beam - open section used - has this beam been designed for torsion. The bearing plate outstand appears large - has this been adequately designed? Potential of instability with hollow core planks in construction stage should be added as a residual CDM risk on all relevant drawings. No CDM design risk register available. Has precambered effect on dead/screed loads been considered? No vertical and plan bracing connection intent provided. | TRUE | FS1018-HEX-ZZ-ZZ-D-S-0602 Structural Sections and Details | FS1018-HEX-ZZ-ZZ-D-S-0602
FS1018-HEX-ZZ-ZZ-D-S-0602 | Structural Sections and Details | P03 | In Progress | 2025-03-28 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-ZZ-ZZ-D-S-0602 Structural Sections and Details | FS1018-HEX-ZZ-ZZ-D-S-0602
FS1018-HEX-ZZ-ZZ-D-S-0801 | 3D Views | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-28 | Please review in light of other comments, particularly overall stability/bracing, separation joints/ movement joints etc. Is there an intention for a separation joint along GL - S? | TRUE | FS1018-HEX-ZZ-ZZ-D-S-0801 3D Views | FS1018-HEX-ZZ-ZZ-D-S-0801
FS1018-HEX-ZZ-ZZ-D-S-0801 | 3D Views | P01 | In Progress | 2025-03-28 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-ZZ-ZZ-D-S-0801 3D Views | FS1018-HEX-ZZ-ZZ-D-S-0801
FS1018-HEX-ZZ-ZZ-M-C-0001 | Native Civil Model | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-16 | Issued on Splash sheet as S3, please ensure when it's issued for Acceptance it's in S5 status. Miss Alignment of model in splash sheet | TRUE | FS1018-HEX-ZZ-ZZ-M-C-0001 Native Civil Model | FS1018-HEX-ZZ-ZZ-M-C-0001
FS1018-HEX-ZZ-ZZ-M-C-0001 | Native Civil Model | P02 | In Progress | 2025-04-16 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-ZZ-ZZ-M-C-0001 Native Civil Model | FS1018-HEX-ZZ-ZZ-M-C-0001
FS1018-HEX-ZZ-ZZ-M-C-0002 | IFC SPF Civil Model | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-16 |  | TRUE | FS1018-HEX-ZZ-ZZ-M-C-0002 IFC SPF Civil Model | FS1018-HEX-ZZ-ZZ-M-C-0002
FS1018-HEX-ZZ-ZZ-M-C-0003 | Navisworks Civil Model | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-16 |  | TRUE | FS1018-HEX-ZZ-ZZ-M-C-0003 Navisworks Civil Model | FS1018-HEX-ZZ-ZZ-M-C-0003
FS1018-HEX-ZZ-ZZ-M-S-0001 | Native Structural Model | P09 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-16 | Issued on Splash sheet as S1 for coordination, please ensure when it's issued for Acceptance it's in S5 status | TRUE | FS1018-HEX-ZZ-ZZ-M-S-0001 Native Structural Model | FS1018-HEX-ZZ-ZZ-M-S-0001
FS1018-HEX-ZZ-ZZ-M-S-0001 | Native Structural Model | P09 | In Progress | 2025-04-16 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-ZZ-ZZ-M-S-0001 Native Structural Model | FS1018-HEX-ZZ-ZZ-M-S-0001
FS1018-HEX-ZZ-ZZ-M-S-0002 | IFC SPF Structural Model | P09 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-16 |  | TRUE | FS1018-HEX-ZZ-ZZ-M-S-0002 IFC SPF Structural Model | FS1018-HEX-ZZ-ZZ-M-S-0002
FS1018-HEX-ZZ-ZZ-M-S-0003 | Navis Structural Model | P09 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-16 |  | TRUE | FS1018-HEX-ZZ-ZZ-M-S-0003 Navis Structural Model | FS1018-HEX-ZZ-ZZ-M-S-0003
FS1018-HEX-ZZ-ZZ-T-C-0001 | General Notes | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-25 | Drainage Notes: 13. No protection slab detail provided 14. three week appication for Section 106 is a programme and approval risk. Survey and design to be completed prior to application 16. BS EN 295 current standard is 2013. Confirm strength for pipes 150 - 300 as the requirement appears to be 48kN/m Pavement - Geotechnical and pavement risks appear to be passed on to site. Cost, programme risk and responsibility TBC Pavement Notes: 4. Geotechnical and pavement risks appear to be passed on to site. Cost, programme risk and responsibility TBC 5. Should there be an instruction here for testing results to be provided, timescale and design updated accordingly. 6. Works decisions being passed on to site which could bypass the design and review process, Who makes the determination and who takes responsibility? Kerbing notes: Spelling to be checked to reduce confusion. | TRUE | FS1018-HEX-ZZ-ZZ-T-C-0001 General Notes | FS1018-HEX-ZZ-ZZ-T-C-0001
FS1018-HEX-ZZ-ZZ-T-C-0001 | General Notes | P02 | In Progress | 2025-03-25 | Designer Response | Pending |  |  | TRUE | FS1018-HEX-ZZ-ZZ-T-C-0001 General Notes | FS1018-HEX-ZZ-ZZ-T-C-0001
FS1018-MAJ-XX-XX-L-X-0090 | Detailed Responsibility Matrix | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-16 | Does not indicated when the information is to be exchanged and with whom; and which task team is responsible for its production. As per ISO 19650‑2:2018 5.4.2 | TRUE | FS1018-MAJ-XX-XX-L-X-0090 Detailed Responsibility Matrix | FS1018-MAJ-XX-XX-L-X-0090
FS1018-MAJ-XX-XX-L-X-0090 | Detailed Responsibility Matrix | P02 | In Progress | 2025-04-16 | Designer Response | Pending |  |  | TRUE | FS1018-MAJ-XX-XX-L-X-0090 Detailed Responsibility Matrix | FS1018-MAJ-XX-XX-L-X-0090
FS1018-MAJ-XX-XX-L-X-8001 | Asset Register | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-11 | Ensure the colours of the columns used in the 05_Alphanumerical_COBieFields and refer to PIS for naming conventions Facility Tab - Created by NumberOfStoreys & UPRN marked as N/A require details. Floor - Please Correct Name floor convention from 00 to Level 00 Space - Name -naming convention is incorrect - See PIS 5.2.5 Space Nomenclature for correct naming convention. Created by, Category , Floor Name, Zone - Created by , Space name incorrect , Type - Created by , Category, description, asset type, NominalLength, NominalWidth, NominalHeight ,PredefinedType incorrect Component - Name , Created by ,Space, InstallationDate, WarrantyStartDatein correct System - Name , Category ,ComponentNames,Description | TRUE | FS1018-MAJ-XX-XX-L-X-8001 Asset Register | FS1018-MAJ-XX-XX-L-X-8001
FS1018-MAJ-XX-XX-L-X-8001 | Asset Register | P02 | In Progress | 2025-04-11 | Designer Response | Pending |  |  | TRUE | FS1018-MAJ-XX-XX-L-X-8001 Asset Register | FS1018-MAJ-XX-XX-L-X-8001
FS1018-MAJ-XX-XX-L-X-8002 | COBie QC Report | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-16 | See Clarification for FS1018-MAJ-XX-XX-T-X-8001-AssetRegister-P02, On issued address new QC report needs to be issued. Please ensure that the Quality Control (QC) shows the output status for each COBie output reporting against the design criteria specified by the COBie schema | TRUE | FS1018-MAJ-XX-XX-L-X-8002 COBie QC Report | FS1018-MAJ-XX-XX-L-X-8002
FS1018-MAJ-XX-XX-L-X-8002 | COBie QC Report | P02 | In Progress | 2025-04-16 | Designer Response | Pending |  |  | TRUE | FS1018-MAJ-XX-XX-L-X-8002 COBie QC Report | FS1018-MAJ-XX-XX-L-X-8002
FS1018-MAJ-XX-XX-T-X-0001 | BIM Execution Plan | P06 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-16 | AllDiscipline Models need to listed in the BEP All Federated models and models incorprated in Federated model needs to be listed in BEP ALL MIDP and TIDP 's need to be listed in BEP 9.6 Classification - Update as per PIS 4.5.1 Asset Classification 9.10 Maximum File Size - please update BIM file sizes as many of the models are larger than 300MB 9.11 Volume and model division - 9.11 Volume and model division 10.4 Volume Code (Field 3) - Building Volume code as per Project Information Standard 5.1.4 Functional Breakdown Codes 11.1 COBie Workbooks Required - Add Instruction Workbook required 11.6 COBie Data Zones and Zoning Naming - not matching the Project information standards 5.2.6 Zone Nomenclature | TRUE | FS1018-MAJ-XX-XX-T-X-0001 BIM Execution Plan | FS1018-MAJ-XX-XX-T-X-0001
FS1018-MAJ-XX-XX-T-X-0001 | BIM Execution Plan | P06 | In Progress | 2025-04-16 | Designer Response | Pending |  |  | TRUE | FS1018-MAJ-XX-XX-T-X-0001 BIM Execution Plan | FS1018-MAJ-XX-XX-T-X-0001
FS1018-MAJ-XX-XX-T-X-1001 | Information Managers Report | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-16 | Report needs to be done against models issued with submission. Report submitted on older revision of models | TRUE | FS1018-MAJ-XX-XX-T-X-1001 Information Managers Report | FS1018-MAJ-XX-XX-T-X-1001
FS1018-MAJ-XX-XX-T-X-1001 | Information Managers Report | P04 | In Progress | 2025-04-16 | Designer Response | Pending |  |  | TRUE | FS1018-MAJ-XX-XX-T-X-1001 Information Managers Report | FS1018-MAJ-XX-XX-T-X-1001
FS1018-MAJ-ZZ-ZZ-M-X-0001 | Federated Information Model | P06 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-11 | Arch,MEP, FFE not matching IFC iisued. Also not listed on BEP so can't confirm namign conventions. See Asset register lcarifications for COBie data issues Landscape model trees misaligned | TRUE | FS1018-MAJ-ZZ-ZZ-M-X-0001 Federated Information Model | FS1018-MAJ-ZZ-ZZ-M-X-0001
FS1018-MAJ-ZZ-ZZ-M-X-0001 | Federated Information Model | P06 | In Progress | 2025-04-11 | Designer Response | Pending |  |  | TRUE | FS1018-MAJ-ZZ-ZZ-M-X-0001 Federated Information Model | FS1018-MAJ-ZZ-ZZ-M-X-0001
FS1018-OFR-XX-ZZ-G-K-0001 | Fire Strategy Report | P05 | In Progress | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | 1. In Section 5 of the fire strategy, add the justification of the services riser being located within 'Stair 2' within 'Table 6', for the attention of building control. 2. (Table 15) Has the fire service been consulted with regards to the requirements needed for the load bearing capacity of the roads for the fire vehicle used to attend the site in an emergency? As it will affect the civil engineer's design. | TRUE | FS1018-OFR-XX-ZZ-G-K-0001 Fire Strategy Report | FS1018-OFR-XX-ZZ-G-K-0001
FS1018-OFR-XX-ZZ-G-K-0001 | Fire Strategy Report | P05 | In Progress | 2025-03-31 | Designer Response | (HB Only) Comments Acknowledged | 2025-04-04 | OFR Response: 1. Section 5 - Fire Strategy (Table 6) The service riser is located within the lobby rather than within Stair 2. As this design aligns with standard guidance, it does not constitute a deviation and therefore is not included in Table 6. OFR Response: 2. Table 15 - Fire Service Access Response: OFR has outlined the design expectations for fire vehicle access, including load-bearing capacity and dimensional requirements, as detailed in Table 15. These specifications should be adopted by the civil engineer to ensure compliance. HEXA Civil Engineer response: 2. Table 15-Fire Service Access The fire tender access to the site was considered in the development of the pavement build-ups, and as such the build-ups in the areas that anticipate access by a fire tender has been designed accordingly. | TRUE | FS1018-OFR-XX-ZZ-G-K-0001 Fire Strategy Report | FS1018-OFR-XX-ZZ-G-K-0001
FS1018-OFR-XX-ZZ-G-K-0001 | Fire Strategy Report | P05 | In Progress | 2025-04-04 | DFE Review of Responses | Pending |  |  | TRUE | FS1018-OFR-XX-ZZ-G-K-0001 Fire Strategy Report | FS1018-OFR-XX-ZZ-G-K-0001
FS1018-ONE-XX-XX-T-L-0001 | Outline Specification | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-02 | The document does not have the level of detail expected at RIBA stage 4, please provide full specifications for each of the items listed, i.e. for the litter bin, please provide the make and model, the fixings to be used and confirmation of the colour. | TRUE | FS1018-ONE-XX-XX-T-L-0001 Outline Specification | FS1018-ONE-XX-XX-T-L-0001
FS1018-ONE-XX-XX-T-L-0001 | Outline Specification | P04 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-ONE-XX-XX-T-L-0001 Outline Specification | FS1018-ONE-XX-XX-T-L-0001
FS1018-ONE-XX-XX-T-L-0002 | Design Development Schedule | P02 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-ONE-XX-XX-T-L-0002 Design Development Schedule | FS1018-ONE-XX-XX-T-L-0002
FS1018-ONE-XX-ZZ-D-L-0001 | Location Plan | P05 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-03 |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0001 Location Plan | FS1018-ONE-XX-ZZ-D-L-0001
FS1018-ONE-XX-ZZ-D-L-0002 | Existing Site Plan | P07 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-03 |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0002 Existing Site Plan | FS1018-ONE-XX-ZZ-D-L-0002
FS1018-ONE-XX-ZZ-D-L-0003 | Whole Site Plan | P14 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 3.1 please indicate the proposals for the existing storage container 3.2 awaiting proposals for location of kerb-side refuse store 4.1 Areas of landscaping to the perimeter of the building clash with the hardstanding area noted on the architectural drawings required for maintenance of the building. 4.2 Please change the colour for the proposed trees vs existing trees, as mentioned many times, it is difficult to tell the difference. 4.3 Please confirm the status of the tree in the most northern swale, in the TCA car park, as it has a red dotted line to imply that it is being removed but it is also green, which implies it is new – this can not occur as it would be over a drainage pipe. 4.4 Tree over drainage pipe adjacent to parking space 129. 4.5 Please coordinate the drainage plan with the landscaping plans as there are a number of swales on the eastern side of the building which are either shown at different sizes, or not shown at all. Example south of parking bay 16 to the top of the turning head. 4.6 The drainage plan implies that there will be a swale adjacent to the rear of the dining terrace, please confirm if this is correct. 4.7 Please be consistent with fence line colouring. Also, please clarify where the 2.4m high fencing is proposed | TRUE | FS1018-ONE-XX-ZZ-D-L-0003 Whole Site Plan | FS1018-ONE-XX-ZZ-D-L-0003
FS1018-ONE-XX-ZZ-D-L-0003 | Whole Site Plan | P14 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0003 Whole Site Plan | FS1018-ONE-XX-ZZ-D-L-0003
FS1018-ONE-XX-ZZ-D-L-0004 | Site Landscaping Plan 1 of 5 | P07 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 3.1 please indicate the proposals for the existing storage container 3.2 awaiting proposals for location of kerb-side refuse store "4.1 Areas of landscaping to the perimeter of the building clash with the hardstanding area noted on the architectural drawings required for maintenance of the building. " "4.2 Please indicate the gate swing of the existing site access gates. It looks like the proposed pedestrian crossings will clash with the gates when in the open position. " "4.3 Do the refuse collection strategy and the catering delivery require a dropped kerb alongside the service bay to allow for wheeled bins and deliveries trolleys?" 4.4 Please check the level indicator arrows on the pedestrian path from Weasenham Lane. 4.5 Please confirm what the blue bubble to the west of the dining terrace is for? | TRUE | FS1018-ONE-XX-ZZ-D-L-0004 Site Landscaping Plan 1 of 5 | FS1018-ONE-XX-ZZ-D-L-0004
FS1018-ONE-XX-ZZ-D-L-0004 | Site Landscaping Plan 1 of 5 | P07 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0004 Site Landscaping Plan 1 of 5 | FS1018-ONE-XX-ZZ-D-L-0004
FS1018-ONE-XX-ZZ-D-L-0005 | Site Landscaping Plan 2 of 5 | P07 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "3.1 please indicate the proposals for the existing storage container" "3.2 awaiting proposals for location of kerb-sied refuse store" "4.1 Please clarify what the hatched area is to the left of the existing storage container" | TRUE | FS1018-ONE-XX-ZZ-D-L-0005 Site Landscaping Plan 2 of 5 | FS1018-ONE-XX-ZZ-D-L-0005
FS1018-ONE-XX-ZZ-D-L-0005 | Site Landscaping Plan 2 of 5 | P07 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0005 Site Landscaping Plan 2 of 5 | FS1018-ONE-XX-ZZ-D-L-0005
FS1018-ONE-XX-ZZ-D-L-0006 | Site Landscaping Plan 3 of 5 | P07 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "3.1 please indicate the proposals for the existing storage container" "4.1 Areas of landscaping to the perimeter of the building clash with the hardstanding area noted on the architectural drawings required for maintenance of the building. " "4.2 Please clarify what the hatched area is to the left of the existing storage container" 4.3 Please confirm what the blue bubble to the west of the building is for? | TRUE | FS1018-ONE-XX-ZZ-D-L-0006 Site Landscaping Plan 3 of 5 | FS1018-ONE-XX-ZZ-D-L-0006
FS1018-ONE-XX-ZZ-D-L-0006 | Site Landscaping Plan 3 of 5 | P07 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0006 Site Landscaping Plan 3 of 5 | FS1018-ONE-XX-ZZ-D-L-0006
FS1018-ONE-XX-ZZ-D-L-0007 | Site Landscaping Plan 4 of 5 | P07 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 SuDs area is simply coloured and labelled as SuDs in the key. Please indicate the proposals?" 4.2. Please confirm if root protection is actually required for all of the trees on the south east boundary. 4.3. Please review the colouration of the EV charging parking bays as they appear to be shown as Existing Permeable Concrete Block Retained, which is not correct. | TRUE | FS1018-ONE-XX-ZZ-D-L-0007 Site Landscaping Plan 4 of 5 | FS1018-ONE-XX-ZZ-D-L-0007
FS1018-ONE-XX-ZZ-D-L-0007 | Site Landscaping Plan 4 of 5 | P07 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0007 Site Landscaping Plan 4 of 5 | FS1018-ONE-XX-ZZ-D-L-0007
FS1018-ONE-XX-ZZ-D-L-0008 | Site Landscaping Plan 5 of 5 | P07 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 SuDs area is simply coloured and labelled as SuDs in the key. Please indicate the proposals?" "4.2 Please indicate the fence proposals around the sub-station" | TRUE | FS1018-ONE-XX-ZZ-D-L-0008 Site Landscaping Plan 5 of 5 | FS1018-ONE-XX-ZZ-D-L-0008
FS1018-ONE-XX-ZZ-D-L-0008 | Site Landscaping Plan 5 of 5 | P07 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0008 Site Landscaping Plan 5 of 5 | FS1018-ONE-XX-ZZ-D-L-0008
FS1018-ONE-XX-ZZ-D-L-0009 | Access and Security Strategy | P08 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 Please indicate the fence proposals around the sub-station" | TRUE | FS1018-ONE-XX-ZZ-D-L-0009 Access and Security Strategy | FS1018-ONE-XX-ZZ-D-L-0009
FS1018-ONE-XX-ZZ-D-L-0009 | Access and Security Strategy | P08 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0009 Access and Security Strategy | FS1018-ONE-XX-ZZ-D-L-0009
FS1018-ONE-XX-ZZ-D-L-0010 | Circulation Strategy | P06 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 What is the strategy for providing access and parking for the sub-station? How is this compliant with GDB 2.8.1.14 and raise as a derogation if necessary" "4.2 Please add white lining for an additional crossing lining up with northernmost accessible parking bay and running east to the parking space to the eastern run of parking bays." | TRUE | FS1018-ONE-XX-ZZ-D-L-0010 Circulation Strategy | FS1018-ONE-XX-ZZ-D-L-0010
FS1018-ONE-XX-ZZ-D-L-0010 | Circulation Strategy | P06 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0010 Circulation Strategy | FS1018-ONE-XX-ZZ-D-L-0010
FS1018-ONE-XX-ZZ-D-L-0011 | External Sports Provision | P07 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 Please indicate the access points for both TCA and WFS for accessing any shared sports provision" | TRUE | FS1018-ONE-XX-ZZ-D-L-0011 External Sports Provision | FS1018-ONE-XX-ZZ-D-L-0011
FS1018-ONE-XX-ZZ-D-L-0011 | External Sports Provision | P07 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0011 External Sports Provision | FS1018-ONE-XX-ZZ-D-L-0011
FS1018-ONE-XX-ZZ-D-L-0012 | Green Infrastructure Plan | P08 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-01 | Need to confirm if green roof is being included or not and extent of it soo that UGF calculation is complete. | TRUE | FS1018-ONE-XX-ZZ-D-L-0012 Green Infrastructure Plan | FS1018-ONE-XX-ZZ-D-L-0012
FS1018-ONE-XX-ZZ-D-L-0012 | Green Infrastructure Plan | P08 | In Progress | 2025-04-01 | Designer Response | Pending |  |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0012 Green Infrastructure Plan | FS1018-ONE-XX-ZZ-D-L-0012
FS1018-ONE-XX-ZZ-D-L-0013 | BB103 Guidance | P05 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 Please indicate the red line boundary along with the area within the red line boundary." "4.2 Please indicate the historic figures for comparison i.e. control option/ stage 3" | TRUE | FS1018-ONE-XX-ZZ-D-L-0013 BB103 Guidance | FS1018-ONE-XX-ZZ-D-L-0013
FS1018-ONE-XX-ZZ-D-L-0013 | BB103 Guidance | P05 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0013 BB103 Guidance | FS1018-ONE-XX-ZZ-D-L-0013
FS1018-ONE-XX-ZZ-D-L-0014 | Hazard Identification Plan | P06 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 Are there no construction related risks with sharing site access with the temporary school?" "4.2 Are there no hazards relating to enabling works/ highways works for section 1.0?" | TRUE | FS1018-ONE-XX-ZZ-D-L-0014 Hazard Identification Plan | FS1018-ONE-XX-ZZ-D-L-0014
FS1018-ONE-XX-ZZ-D-L-0014 | Hazard Identification Plan | P06 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0014 Hazard Identification Plan | FS1018-ONE-XX-ZZ-D-L-0014
FS1018-ONE-XX-ZZ-D-L-0015 | Refurbishment Remodelling Strategy | P09 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 extent of hard landscaping does not match up with the architectural information - specifically please coordinate the hard standing to the building perimeter for maintenance access." 4.2 Further coordination needed with Portakabin regarding the parking area for Wisbech Free School. | TRUE | FS1018-ONE-XX-ZZ-D-L-0015 Refurbishment Remodelling Strategy | FS1018-ONE-XX-ZZ-D-L-0015
FS1018-ONE-XX-ZZ-D-L-0015 | Refurbishment Remodelling Strategy | P09 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0015 Refurbishment Remodelling Strategy | FS1018-ONE-XX-ZZ-D-L-0015
FS1018-ONE-XX-ZZ-D-L-0017 | Site Sections | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 unable to access the information via Aconex" "4.2 Pedestrian crossings near entrance gates, tactile paving and dropped kerbs are incorrectly shown as areas with no work. " | TRUE | FS1018-ONE-XX-ZZ-D-L-0017 Site Sections | FS1018-ONE-XX-ZZ-D-L-0017
FS1018-ONE-XX-ZZ-D-L-0017 | Site Sections | P03 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0017 Site Sections | FS1018-ONE-XX-ZZ-D-L-0017
FS1018-ONE-XX-ZZ-D-L-0021 | Existing Site Plan 1 of 5 | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-03 |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0021 Existing Site Plan 1 of 5 | FS1018-ONE-XX-ZZ-D-L-0021
FS1018-ONE-XX-ZZ-D-L-0022 | Existing Site Plan 2 of 5 | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-03 |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0022 Existing Site Plan 2 of 5 | FS1018-ONE-XX-ZZ-D-L-0022
FS1018-ONE-XX-ZZ-D-L-0023 | Existing Site Plan 3 of 5 | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-03 |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0023 Existing Site Plan 3 of 5 | FS1018-ONE-XX-ZZ-D-L-0023
FS1018-ONE-XX-ZZ-D-L-0024 | Existing Site Plan 4 of 5 | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-03 |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0024 Existing Site Plan 4 of 5 | FS1018-ONE-XX-ZZ-D-L-0024
FS1018-ONE-XX-ZZ-D-L-0025 | Existing Site Plan 5 of 5 | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-03 |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0025 Existing Site Plan 5 of 5 | FS1018-ONE-XX-ZZ-D-L-0025
FS1018-ONE-XX-ZZ-D-L-0201 | Detailed Planting Plan Sheet 1 of 5 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 Soft landscaping clashes with the hard standing zone for maintenance access to the building perimeter shown on the architectural drawings" 4.2 Please coordinate the drainage plan with the landscaping plans as there are a number of swales on the eastern side of the building which are either shown at different sizes, or not shown at all. Example south of parking bay 16 to the top of the turning head. | TRUE | FS1018-ONE-XX-ZZ-D-L-0201 Detailed Planting Plan Sheet 1 of 5 | FS1018-ONE-XX-ZZ-D-L-0201
FS1018-ONE-XX-ZZ-D-L-0201 | Detailed Planting Plan Sheet 1 of 5 | P03 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0201 Detailed Planting Plan Sheet 1 of 5 | FS1018-ONE-XX-ZZ-D-L-0201
FS1018-ONE-XX-ZZ-D-L-0202 | Detailed Planting Plan Sheet 2 of 5 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 How is the habitat area defined in terms of planting?" | TRUE | FS1018-ONE-XX-ZZ-D-L-0202 Detailed Planting Plan Sheet 2 of 5 | FS1018-ONE-XX-ZZ-D-L-0202
FS1018-ONE-XX-ZZ-D-L-0202 | Detailed Planting Plan Sheet 2 of 5 | P03 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0202 Detailed Planting Plan Sheet 2 of 5 | FS1018-ONE-XX-ZZ-D-L-0202
FS1018-ONE-XX-ZZ-D-L-0203 | Detailed Planting Plan Sheet 3 of 5 | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 Soft landscaping clashes with the hard standing zone for maintenance access to the building perimeter shown on the architectural drawings" | TRUE | FS1018-ONE-XX-ZZ-D-L-0203 Detailed Planting Plan Sheet 3 of 5 | FS1018-ONE-XX-ZZ-D-L-0203
FS1018-ONE-XX-ZZ-D-L-0203 | Detailed Planting Plan Sheet 3 of 5 | P04 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0203 Detailed Planting Plan Sheet 3 of 5 | FS1018-ONE-XX-ZZ-D-L-0203
FS1018-ONE-XX-ZZ-D-L-0204 | Detailed Planting Plan Sheet 4 of 5 | P03 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-03 |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0204 Detailed Planting Plan Sheet 4 of 5 | FS1018-ONE-XX-ZZ-D-L-0204
FS1018-ONE-XX-ZZ-D-L-0205 | Detailed Planting Plan Sheet 5 of 5 | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Shrubs should not be planted in the swale to the north of the TCA car park. | TRUE | FS1018-ONE-XX-ZZ-D-L-0205 Detailed Planting Plan Sheet 5 of 5 | FS1018-ONE-XX-ZZ-D-L-0205
FS1018-ONE-XX-ZZ-D-L-0205 | Detailed Planting Plan Sheet 5 of 5 | P04 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0205 Detailed Planting Plan Sheet 5 of 5 | FS1018-ONE-XX-ZZ-D-L-0205
FS1018-ONE-XX-ZZ-D-L-0401 | Outline Levels Plan 1 of 5 | P07 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-03 |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0401 Outline Levels Plan 1 of 5 | FS1018-ONE-XX-ZZ-D-L-0401
FS1018-ONE-XX-ZZ-D-L-0402 | Outline Levels Plan 2 of 5 | P07 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-03 |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0402 Outline Levels Plan 2 of 5 | FS1018-ONE-XX-ZZ-D-L-0402
FS1018-ONE-XX-ZZ-D-L-0403 | Outline Levels Plan 3 of 5 | P07 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-04-03 |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0403 Outline Levels Plan 3 of 5 | FS1018-ONE-XX-ZZ-D-L-0403
FS1018-ONE-XX-ZZ-D-L-0404 | Outline Levels Plan 4 of 5 | P06 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 Please indicate levels proposals for the swale" | TRUE | FS1018-ONE-XX-ZZ-D-L-0404 Outline Levels Plan 4 of 5 | FS1018-ONE-XX-ZZ-D-L-0404
FS1018-ONE-XX-ZZ-D-L-0404 | Outline Levels Plan 4 of 5 | P06 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0404 Outline Levels Plan 4 of 5 | FS1018-ONE-XX-ZZ-D-L-0404
FS1018-ONE-XX-ZZ-D-L-0405 | Outline Levels Plan 5 of 5 | P06 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 Please indicate levels proposals for the swale" | TRUE | FS1018-ONE-XX-ZZ-D-L-0405 Outline Levels Plan 5 of 5 | FS1018-ONE-XX-ZZ-D-L-0405
FS1018-ONE-XX-ZZ-D-L-0405 | Outline Levels Plan 5 of 5 | P06 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0405 Outline Levels Plan 5 of 5 | FS1018-ONE-XX-ZZ-D-L-0405
FS1018-ONE-XX-ZZ-D-L-0601 | Landscape Details Sheet 1 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 Section 2 has the curved part of the canopy structure missing" | TRUE | FS1018-ONE-XX-ZZ-D-L-0601 Landscape Details Sheet 1 | FS1018-ONE-XX-ZZ-D-L-0601
FS1018-ONE-XX-ZZ-D-L-0601 | Landscape Details Sheet 1 | P03 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0601 Landscape Details Sheet 1 | FS1018-ONE-XX-ZZ-D-L-0601
FS1018-ONE-XX-ZZ-D-L-0602 | Landscape Details Sheet 2 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | 4.1 Lack of information on the foundation detail. | TRUE | FS1018-ONE-XX-ZZ-D-L-0602 Landscape Details Sheet 2 | FS1018-ONE-XX-ZZ-D-L-0602
FS1018-ONE-XX-ZZ-D-L-0602 | Landscape Details Sheet 2 | P03 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0602 Landscape Details Sheet 2 | FS1018-ONE-XX-ZZ-D-L-0602
FS1018-ONE-XX-ZZ-D-L-0603 | Landscape Details Sheet 3 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-03 | "4.1 Please indicate the type of timber cladding proposed" | TRUE | FS1018-ONE-XX-ZZ-D-L-0603 Landscape Details Sheet 3 | FS1018-ONE-XX-ZZ-D-L-0603
FS1018-ONE-XX-ZZ-D-L-0603 | Landscape Details Sheet 3 | P03 | In Progress | 2025-04-03 | Designer Response | Pending |  |  | TRUE | FS1018-ONE-XX-ZZ-D-L-0603 Landscape Details Sheet 3 | FS1018-ONE-XX-ZZ-D-L-0603
FS1018-ONE-ZZ-XX-T-L-0004 | Security Statement | P02 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-ONE-ZZ-XX-T-L-0004 Security Statement | FS1018-ONE-ZZ-XX-T-L-0004
FS1018-ONE-ZZ-ZZ-M-L-0001 | Landscape Model | P03 | Completed | 2025-04-14 | DFE Review | A - Accepted | 2025-04-14 |  | TRUE | FS1018-ONE-ZZ-ZZ-M-L-0001 Landscape Model | FS1018-ONE-ZZ-ZZ-M-L-0001
FS1018-ONE-ZZ-ZZ-M-L-0002 | Landscape Model | P03 | Completed | 2025-04-14 | DFE Review | A - Accepted | 2025-04-14 |  | TRUE | FS1018-ONE-ZZ-ZZ-M-L-0002 Landscape Model | FS1018-ONE-ZZ-ZZ-M-L-0002
FS1018-ONE-ZZ-ZZ-M-L-0003 | Landscape Model | P03 | Completed | 2025-04-14 | DFE Review | A - Accepted | 2025-04-14 |  | TRUE | FS1018-ONE-ZZ-ZZ-M-L-0003 Landscape Model | FS1018-ONE-ZZ-ZZ-M-L-0003
FS1018-PIN-XX-XX-L-O-0003 | Task Team Risk Register | P02 | In Progress | 2025-03-13 | DFE Review | Pending |  |  | TRUE | FS1018-PIN-XX-XX-L-O-0003 Task Team Risk Register | FS1018-PIN-XX-XX-L-O-0003
FS1018-PIN-ZZ-00-D-O-0001 | Ground Floor GA 1 Of 2 | P05 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Update based on review comments. | TRUE | FS1018-PIN-ZZ-00-D-O-0001 Ground Floor GA 1 Of 2 | FS1018-PIN-ZZ-00-D-O-0001
FS1018-PIN-ZZ-00-D-O-0001 | Ground Floor GA 1 Of 2 | P05 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-0001 Ground Floor GA 1 Of 2 | FS1018-PIN-ZZ-00-D-O-0001
FS1018-PIN-ZZ-00-D-O-0002 | Ground Floor GA 2 Of 2 | P05 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Update based on review comments. | TRUE | FS1018-PIN-ZZ-00-D-O-0002 Ground Floor GA 2 Of 2 | FS1018-PIN-ZZ-00-D-O-0002
FS1018-PIN-ZZ-00-D-O-0002 | Ground Floor GA 2 Of 2 | P05 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-0002 Ground Floor GA 2 Of 2 | FS1018-PIN-ZZ-00-D-O-0002
FS1018-PIN-ZZ-00-D-O-0006 | Lobby 1 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1. Can a detailed drawing of the reception hatch reception be provided? | TRUE | FS1018-PIN-ZZ-00-D-O-0006 Lobby 1 | FS1018-PIN-ZZ-00-D-O-0006
FS1018-PIN-ZZ-00-D-O-0006 | Lobby 1 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-0006 Lobby 1 | FS1018-PIN-ZZ-00-D-O-0006
FS1018-PIN-ZZ-00-D-O-0601 | Food Prep Area, Kitchen Servery And Wash Up 1 | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Spur shelving 2 tier racking, impeding access to external double doors. 2.Hand wash station should be closer to external doors. 3.Can the office area be accessed or form part of the off dry store to reduce number of doors and free up walls/dead space in kitchen area. 4.Door swing to cold room is missing of drawing. 5. What is the servery and hot/cold provision sufficient for number of pupils moving through? " | TRUE | FS1018-PIN-ZZ-00-D-O-0601 Food Prep Area, Kitchen Servery And Wash Up 1 | FS1018-PIN-ZZ-00-D-O-0601
FS1018-PIN-ZZ-00-D-O-0601 | Food Prep Area, Kitchen Servery And Wash Up 1 | P04 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-0601 Food Prep Area, Kitchen Servery And Wash Up 1 | FS1018-PIN-ZZ-00-D-O-0601
FS1018-PIN-ZZ-00-D-O-1109 | Music Room | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Only space for 14 keyboards allowed, should this be 15? Could the store room door be moved toward window to allow for an additional keyboard. 2. 2.Can the DDA desk to be one of the desks that face the whiteboard? | TRUE | FS1018-PIN-ZZ-00-D-O-1109 Music Room | FS1018-PIN-ZZ-00-D-O-1109
FS1018-PIN-ZZ-00-D-O-1109 | Music Room | P04 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-1109 Music Room | FS1018-PIN-ZZ-00-D-O-1109
FS1018-PIN-ZZ-00-D-O-1110 | DT Workshop 1 | P05 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Is there sufficient circulation space between machines and desks. 2. Please add dimensions to all equipment 3. Can the desk layout be better utilised, perhaps rotating the desks 45 degrees so pupils don’t have their back to the whiteboard. With the DDA desk better located near the whiteboard and the teacher not with their back to one of the benches? | TRUE | FS1018-PIN-ZZ-00-D-O-1110 DT Workshop 1 | FS1018-PIN-ZZ-00-D-O-1110
FS1018-PIN-ZZ-00-D-O-1110 | DT Workshop 1 | P05 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-1110 DT Workshop 1 | FS1018-PIN-ZZ-00-D-O-1110
FS1018-PIN-ZZ-00-D-O-1111 | Food Room 1 Option 1 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1. Can the desk be moved to the end and rotated to face the whiteboard, with another circulation for access? 2.Can the handwash be moved from behind the door? 3.Can an extra sink be included here? 4. These sections are not reflective of the floor plan | TRUE | FS1018-PIN-ZZ-00-D-O-1111 Food Room 1 Option 1 | FS1018-PIN-ZZ-00-D-O-1111
FS1018-PIN-ZZ-00-D-O-1111 | Food Room 1 Option 1 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-1111 Food Room 1 Option 1 | FS1018-PIN-ZZ-00-D-O-1111
FS1018-PIN-ZZ-00-D-O-1112 | DT Studio Graphic Products | P07 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.The classroom does not accommodate the 28 pupils as per the school request. | TRUE | FS1018-PIN-ZZ-00-D-O-1112 DT Studio Graphic Products | FS1018-PIN-ZZ-00-D-O-1112
FS1018-PIN-ZZ-00-D-O-1112 | DT Studio Graphic Products | P07 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-1112 DT Studio Graphic Products | FS1018-PIN-ZZ-00-D-O-1112
FS1018-PIN-ZZ-00-D-O-1113 | DT Studio Electronics And Control | P07 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Can the DDA desk be moved to face the whiteboard, with enough circulation space to access? | TRUE | FS1018-PIN-ZZ-00-D-O-1113 DT Studio Electronics And Control | FS1018-PIN-ZZ-00-D-O-1113
FS1018-PIN-ZZ-00-D-O-1113 | DT Studio Electronics And Control | P07 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-1113 DT Studio Electronics And Control | FS1018-PIN-ZZ-00-D-O-1113
FS1018-PIN-ZZ-00-D-O-1211 | Food Room 1 | P05 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1. Is the DDA kitchen compliant with prep space required next to the hob area -600mm? 2. The DDA desk is not near the DDA kitchen, can this be relocated? 3. Does the hand sink need to be directly behind the door, can this be switched with coat hooks? 4. Currently there is central cluster of 3x hobs with no sinks, can these be better distributed? | TRUE | FS1018-PIN-ZZ-00-D-O-1211 Food Room 1 | FS1018-PIN-ZZ-00-D-O-1211
FS1018-PIN-ZZ-00-D-O-1211 | Food Room 1 | P05 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-1211 Food Room 1 | FS1018-PIN-ZZ-00-D-O-1211
FS1018-PIN-ZZ-00-D-O-2001 | Assembly Hall, Dining Layout | P07 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-07 | Seating capacity is listed as 138 but shows seating for 144. As all pupils need to be seating for lunch, please indicate how this is achieved within the lunch time period and the current seating provided. If more tables are required, can this be accommodated? | TRUE | FS1018-PIN-ZZ-00-D-O-2001 Assembly Hall, Dining Layout | FS1018-PIN-ZZ-00-D-O-2001
FS1018-PIN-ZZ-00-D-O-2001 | Assembly Hall, Dining Layout | P07 | In Progress | 2025-04-07 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-2001 Assembly Hall, Dining Layout | FS1018-PIN-ZZ-00-D-O-2001
FS1018-PIN-ZZ-00-D-O-2002 | Sports Hall Exam Layout | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Please update the store room layout to current layout provided. | TRUE | FS1018-PIN-ZZ-00-D-O-2002 Sports Hall Exam Layout | FS1018-PIN-ZZ-00-D-O-2002
FS1018-PIN-ZZ-00-D-O-2002 | Sports Hall Exam Layout | P04 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-2002 Sports Hall Exam Layout | FS1018-PIN-ZZ-00-D-O-2002
FS1018-PIN-ZZ-00-D-O-2003 | Assembly Hall, Assembly Layout | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-07 | 1.Please demonstrate the SOA capacity in the drawing? 2. Can the refrigerated servery units be relocated when not in use? 3.Where are the chairs being stored when not in use, not shown in drawings? | TRUE | FS1018-PIN-ZZ-00-D-O-2003 Assembly Hall, Assembly Layout | FS1018-PIN-ZZ-00-D-O-2003
FS1018-PIN-ZZ-00-D-O-2003 | Assembly Hall, Assembly Layout | P04 | In Progress | 2025-04-07 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-2003 Assembly Hall, Assembly Layout | FS1018-PIN-ZZ-00-D-O-2003
FS1018-PIN-ZZ-00-D-O-3002 | Sports Hall Sport Layout | P05 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-00-D-O-3002 Sports Hall Sport Layout | FS1018-PIN-ZZ-00-D-O-3002
FS1018-PIN-ZZ-00-D-O-3004 | LRC | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Can the floor swing be flipped and the door be moved to the right to improve circulation in the space? | TRUE | FS1018-PIN-ZZ-00-D-O-3004 LRC | FS1018-PIN-ZZ-00-D-O-3004
FS1018-PIN-ZZ-00-D-O-3004 | LRC | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-3004 LRC | FS1018-PIN-ZZ-00-D-O-3004
FS1018-PIN-ZZ-00-D-O-4003 | Enclosed Office, Admin Head 1 | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Is there potential to switch seating and desk area, to avoid glare from the the window? | TRUE | FS1018-PIN-ZZ-00-D-O-4003 Enclosed Office, Admin Head 1 | FS1018-PIN-ZZ-00-D-O-4003
FS1018-PIN-ZZ-00-D-O-4003 | Enclosed Office, Admin Head 1 | P02 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-4003 Enclosed Office, Admin Head 1 | FS1018-PIN-ZZ-00-D-O-4003
FS1018-PIN-ZZ-00-D-O-4004 | Enclosed Office, Admin PA 1 | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-00-D-O-4004 Enclosed Office, Admin PA 1 | FS1018-PIN-ZZ-00-D-O-4004
FS1018-PIN-ZZ-00-D-O-4005 | Reprographics Room 1 | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-00-D-O-4005 Reprographics Room 1 | FS1018-PIN-ZZ-00-D-O-4005
FS1018-PIN-ZZ-00-D-O-4006 | Enclosed Office, With Recep Desk And Window 1 | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Can more space be provided to the desks at the reception desk , taken from the row behind? | TRUE | FS1018-PIN-ZZ-00-D-O-4006 Enclosed Office, With Recep Desk And Window 1 | FS1018-PIN-ZZ-00-D-O-4006
FS1018-PIN-ZZ-00-D-O-4006 | Enclosed Office, With Recep Desk And Window 1 | P02 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-4006 Enclosed Office, With Recep Desk And Window 1 | FS1018-PIN-ZZ-00-D-O-4006
FS1018-PIN-ZZ-00-D-O-4008 | Reception Area, Entrance 50% Circulation | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Rejected, due to concerns raised around the arrangement of the secure line, furniture layout may need to be change. | TRUE | FS1018-PIN-ZZ-00-D-O-4008 Reception Area, Entrance 50% Circulation | FS1018-PIN-ZZ-00-D-O-4008
FS1018-PIN-ZZ-00-D-O-4008 | Reception Area, Entrance 50% Circulation | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-4008 Reception Area, Entrance 50% Circulation | FS1018-PIN-ZZ-00-D-O-4008
FS1018-PIN-ZZ-00-D-O-4009 | Confidential Meeting Room Interview 1 | P03 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-00-D-O-4009 Confidential Meeting Room Interview 1 | FS1018-PIN-ZZ-00-D-O-4009
FS1018-PIN-ZZ-00-D-O-4015 | Office With Meeting Area, 2 Person 4 | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | One of the walls is missing from the drawing, please can you update so that it is clear. | TRUE | FS1018-PIN-ZZ-00-D-O-4015 Office With Meeting Area, 2 Person 4 | FS1018-PIN-ZZ-00-D-O-4015
FS1018-PIN-ZZ-00-D-O-4015 | Office With Meeting Area, 2 Person 4 | P02 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-4015 Office With Meeting Area, 2 Person 4 | FS1018-PIN-ZZ-00-D-O-4015
FS1018-PIN-ZZ-00-D-O-4018 | Staff Workroom Premises 1 And Equipment Store, Maintenance 1 | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-00-D-O-4018 Staff Workroom Premises 1 And Equipment Store, Maintenance 1 | FS1018-PIN-ZZ-00-D-O-4018
FS1018-PIN-ZZ-00-D-O-5003 | Confidential Meeting Room Interview 1 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Rejected, due to concerns raised around the arrangement of the secure line, furniture layout may need to be change. | TRUE | FS1018-PIN-ZZ-00-D-O-5003 Confidential Meeting Room Interview 1 | FS1018-PIN-ZZ-00-D-O-5003
FS1018-PIN-ZZ-00-D-O-5003 | Confidential Meeting Room Interview 1 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-5003 Confidential Meeting Room Interview 1 | FS1018-PIN-ZZ-00-D-O-5003
FS1018-PIN-ZZ-00-D-O-5007 | DT Prep Room 1 | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-00-D-O-5007 DT Prep Room 1 | FS1018-PIN-ZZ-00-D-O-5007
FS1018-PIN-ZZ-00-D-O-5008 | Food Prep Room 1 | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-00-D-O-5008 Food Prep Room 1 | FS1018-PIN-ZZ-00-D-O-5008
FS1018-PIN-ZZ-00-D-O-5009 | Teaching Resources Store Off DT Studio | P03 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-00-D-O-5009 Teaching Resources Store Off DT Studio | FS1018-PIN-ZZ-00-D-O-5009
FS1018-PIN-ZZ-00-D-O-5011 | Teaching Resources Store Off DT Studio | P03 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-00-D-O-5011 Teaching Resources Store Off DT Studio | FS1018-PIN-ZZ-00-D-O-5011
FS1018-PIN-ZZ-00-D-O-5013 | Teaching Resources Store Music 1 | P03 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-00-D-O-5013 Teaching Resources Store Music 1 | FS1018-PIN-ZZ-00-D-O-5013
FS1018-PIN-ZZ-00-D-O-5018 | Sports Equipment Store, Internal Sports Hall 1 | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-00-D-O-5018 Sports Equipment Store, Internal Sports Hall 1 | FS1018-PIN-ZZ-00-D-O-5018
FS1018-PIN-ZZ-00-D-O-5019 | Sports Equipment Store, External 1 | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-00-D-O-5019 Sports Equipment Store, External 1 | FS1018-PIN-ZZ-00-D-O-5019
FS1018-PIN-ZZ-00-D-O-5103 | Secure Storeroom 1 | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-00-D-O-5103 Secure Storeroom 1 | FS1018-PIN-ZZ-00-D-O-5103
FS1018-PIN-ZZ-00-D-O-5109 | Coats And Bag Store Lockers 1 | P03 | In Progress | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Appreciate the trust has specifically removed these. Please indicate on each locker drawing the location of the lockers and quantity of lockers that could be provided in that area if later required, with the overall number of lockers also listed for reference. | TRUE | FS1018-PIN-ZZ-00-D-O-5109 Coats And Bag Store Lockers 1 | FS1018-PIN-ZZ-00-D-O-5109
FS1018-PIN-ZZ-00-D-O-5109 | Coats And Bag Store Lockers 1 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-5109 Coats And Bag Store Lockers 1 | FS1018-PIN-ZZ-00-D-O-5109
FS1018-PIN-ZZ-00-D-O-5114 | Cleaners Store | P03 | In Progress | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Update title to cleaners store 1 | TRUE | FS1018-PIN-ZZ-00-D-O-5114 Cleaners Store | FS1018-PIN-ZZ-00-D-O-5114
FS1018-PIN-ZZ-00-D-O-5114 | Cleaners Store | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-5114 Cleaners Store | FS1018-PIN-ZZ-00-D-O-5114
FS1018-PIN-ZZ-00-D-O-5117 | Cleaners Store | P03 | In Progress | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Update title to cleaners store 4 | TRUE | FS1018-PIN-ZZ-00-D-O-5117 Cleaners Store | FS1018-PIN-ZZ-00-D-O-5117
FS1018-PIN-ZZ-00-D-O-5117 | Cleaners Store | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-5117 Cleaners Store | FS1018-PIN-ZZ-00-D-O-5117
FS1018-PIN-ZZ-00-D-O-6001 | Dining And Catering | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Has a noticeboard been provided (BOA001) 2. The refrigerated servery are located away from he canteen.Is there an agreed plan of how pupils queue and move through the canteen space. 3.Are 3x tills required and should two of the tills sit back to back to provide better circulation, there is a column in front of the first till. | TRUE | FS1018-PIN-ZZ-00-D-O-6001 Dining And Catering | FS1018-PIN-ZZ-00-D-O-6001
FS1018-PIN-ZZ-00-D-O-6001 | Dining And Catering | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-6001 Dining And Catering | FS1018-PIN-ZZ-00-D-O-6001
FS1018-PIN-ZZ-00-D-O-6002 | Office, Kitchen 1 | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Can the office area be accessed or form part of the off dry store to reduce number of doors and free up walls/dead space in kitchen area. | TRUE | FS1018-PIN-ZZ-00-D-O-6002 Office, Kitchen 1 | FS1018-PIN-ZZ-00-D-O-6002
FS1018-PIN-ZZ-00-D-O-6002 | Office, Kitchen 1 | P02 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-6002 Office, Kitchen 1 | FS1018-PIN-ZZ-00-D-O-6002
FS1018-PIN-ZZ-00-D-O-6003 | Food Store, Kitchen Dry 1 | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Can the office area be accessed or form part of the off dry store to reduce number of doors and free up walls/dead space in kitchen area. | TRUE | FS1018-PIN-ZZ-00-D-O-6003 Food Store, Kitchen Dry 1 | FS1018-PIN-ZZ-00-D-O-6003
FS1018-PIN-ZZ-00-D-O-6003 | Food Store, Kitchen Dry 1 | P02 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-6003 Food Store, Kitchen Dry 1 | FS1018-PIN-ZZ-00-D-O-6003
FS1018-PIN-ZZ-00-D-O-6004 | Cold Store, Kitchen 1 | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | SOA is 2.5m2 however door to freezer reduces useable space | TRUE | FS1018-PIN-ZZ-00-D-O-6004 Cold Store, Kitchen 1 | FS1018-PIN-ZZ-00-D-O-6004
FS1018-PIN-ZZ-00-D-O-6004 | Cold Store, Kitchen 1 | P02 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-6004 Cold Store, Kitchen 1 | FS1018-PIN-ZZ-00-D-O-6004
FS1018-PIN-ZZ-00-D-O-6005 | Cold Store, Kitchen Freezer 1 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Incorrect drawing. Needs updating to reflect new design. | TRUE | FS1018-PIN-ZZ-00-D-O-6005 Cold Store, Kitchen Freezer 1 | FS1018-PIN-ZZ-00-D-O-6005
FS1018-PIN-ZZ-00-D-O-6005 | Cold Store, Kitchen Freezer 1 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-6005 Cold Store, Kitchen Freezer 1 | FS1018-PIN-ZZ-00-D-O-6005
FS1018-PIN-ZZ-00-D-O-6006 | Toilet (With Changing Area) 1 | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1. Toilet should be separate from the changing area, 2.The COSHH cabinet should be located elsewhere. | TRUE | FS1018-PIN-ZZ-00-D-O-6006 Toilet (With Changing Area) 1 | FS1018-PIN-ZZ-00-D-O-6006
FS1018-PIN-ZZ-00-D-O-6006 | Toilet (With Changing Area) 1 | P02 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-6006 Toilet (With Changing Area) 1 | FS1018-PIN-ZZ-00-D-O-6006
FS1018-PIN-ZZ-00-D-O-6007 | Changing Room, With Showers Pupils 1 And Toilets, Suite Pupils, Other 1 | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Update GA to reflect 2. Does the occupancy allow for 38 pupils as per the SOA. It appears only 33 have been allowed for. It appears there is sufficent space to add extra benching to come closer to the SOA requirement of 38. 3. Can circulation space be dimensioned including shower area to enable us to review? | TRUE | FS1018-PIN-ZZ-00-D-O-6007 Changing Room, With Showers Pupils 1 And Toilets, Suite Pupils, Other 1 | FS1018-PIN-ZZ-00-D-O-6007
FS1018-PIN-ZZ-00-D-O-6007 | Changing Room, With Showers Pupils 1 And Toilets, Suite Pupils, Other 1 | P04 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-6007 Changing Room, With Showers Pupils 1 And Toilets, Suite Pupils, Other 1 | FS1018-PIN-ZZ-00-D-O-6007
FS1018-PIN-ZZ-00-D-O-6008 | Changing Room, With Showers Pupils 2 And Toilets, Suite Pupils, Other 2 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Update GA to reflect 2. Does the occupancy allow for 38 pupils as per the SOA. It appears only 33 have been allowed for. It appears there is sufficent space to add extra benching to come closer to the SOA requirement of 38. 3. Can circulation space be dimensioned including shower area to enable us to review? | TRUE | FS1018-PIN-ZZ-00-D-O-6008 Changing Room, With Showers Pupils 2 And Toilets, Suite Pupils, Other 2 | FS1018-PIN-ZZ-00-D-O-6008
FS1018-PIN-ZZ-00-D-O-6008 | Changing Room, With Showers Pupils 2 And Toilets, Suite Pupils, Other 2 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-6008 Changing Room, With Showers Pupils 2 And Toilets, Suite Pupils, Other 2 | FS1018-PIN-ZZ-00-D-O-6008
FS1018-PIN-ZZ-00-D-O-6009 | Music Practice Room 2 | P04 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-00-D-O-6009 Music Practice Room 2 | FS1018-PIN-ZZ-00-D-O-6009
FS1018-PIN-ZZ-00-D-O-6011 | Hygiene Room 1 | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-00-D-O-6011 Hygiene Room 1 | FS1018-PIN-ZZ-00-D-O-6011
FS1018-PIN-ZZ-00-D-O-6042 | First Aid Post Sick Bay 1 And Stairway 7 | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-00-D-O-6042 First Aid Post Sick Bay 1 And Stairway 7 | FS1018-PIN-ZZ-00-D-O-6042
FS1018-PIN-ZZ-00-D-O-6069 | Circulation Space Horizontal On And Coats And Bag Store Lockers 1 | P02 | In Progress | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Appreciate the trust has specifically removed these. Please indicate on each locker drawing the location of the lockers and quantity of lockers that could be provided in that area if later required, with the overall number of lockers also listed for reference. | TRUE | FS1018-PIN-ZZ-00-D-O-6069 Circulation Space Horizontal On And Coats And Bag Store Lockers 1 | FS1018-PIN-ZZ-00-D-O-6069
FS1018-PIN-ZZ-00-D-O-6069 | Circulation Space Horizontal On And Coats And Bag Store Lockers 1 | P02 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-6069 Circulation Space Horizontal On And Coats And Bag Store Lockers 1 | FS1018-PIN-ZZ-00-D-O-6069
FS1018-PIN-ZZ-00-D-O-7001 | Dining And Catering 3D | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Commented on separate drawings. Please revise. | TRUE | FS1018-PIN-ZZ-00-D-O-7001 Dining And Catering 3D | FS1018-PIN-ZZ-00-D-O-7001
FS1018-PIN-ZZ-00-D-O-7001 | Dining And Catering 3D | P04 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-7001 Dining And Catering 3D | FS1018-PIN-ZZ-00-D-O-7001
FS1018-PIN-ZZ-00-D-O-7003 | Dishwashing | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Can the door better be located to improve circulation space, due to location of tills? This comment forms part of multiple other comments around the kitchen layout and design. | TRUE | FS1018-PIN-ZZ-00-D-O-7003 Dishwashing | FS1018-PIN-ZZ-00-D-O-7003
FS1018-PIN-ZZ-00-D-O-7003 | Dishwashing | P04 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-7003 Dishwashing | FS1018-PIN-ZZ-00-D-O-7003
FS1018-PIN-ZZ-00-D-O-7101 | Food Prep Area, Kitchen Servery And Wash Up 1 Electrical Plan | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-02 | Isolators required for full height fridges, as isolation not accessible | TRUE | FS1018-PIN-ZZ-00-D-O-7101 Food Prep Area, Kitchen Servery And Wash Up 1 Electrical Plan | FS1018-PIN-ZZ-00-D-O-7101
FS1018-PIN-ZZ-00-D-O-7101 | Food Prep Area, Kitchen Servery And Wash Up 1 Electrical Plan | P03 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-7101 Food Prep Area, Kitchen Servery And Wash Up 1 Electrical Plan | FS1018-PIN-ZZ-00-D-O-7101
FS1018-PIN-ZZ-00-D-O-7201 | Food Prep Area, Kitchen Servery And Wash Up 1 Electrical Elevations | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-02 | Isolators required for full height fridges, as isolation not accessible | TRUE | FS1018-PIN-ZZ-00-D-O-7201 Food Prep Area, Kitchen Servery And Wash Up 1 Electrical Elevations | FS1018-PIN-ZZ-00-D-O-7201
FS1018-PIN-ZZ-00-D-O-7201 | Food Prep Area, Kitchen Servery And Wash Up 1 Electrical Elevations | P03 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-7201 Food Prep Area, Kitchen Servery And Wash Up 1 Electrical Elevations | FS1018-PIN-ZZ-00-D-O-7201
FS1018-PIN-ZZ-00-D-O-7301 | Food Prep Area, Kitchen Servery And Wash Up 1 Mechanical Plan | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-02 | 1. No section lines for elevations 2. There is no drinking water, cold water is from a boosted cold water system, see AGL drawings 3. Service drops to whb on grid line 3A / B are in correct refer to AGL water / drainage drawings 4. Misspelling of tundish 5. Supply to to water boiler on AGL drawings indicate 15 and no 22 6. Unit clashing with doorway 7. AGL services to adjust to new appliance location 8. Floor gully (G), who is positioning the gully? AGL or Pinnacle? | TRUE | FS1018-PIN-ZZ-00-D-O-7301 Food Prep Area, Kitchen Servery And Wash Up 1 Mechanical Plan | FS1018-PIN-ZZ-00-D-O-7301
FS1018-PIN-ZZ-00-D-O-7301 | Food Prep Area, Kitchen Servery And Wash Up 1 Mechanical Plan | P03 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-7301 Food Prep Area, Kitchen Servery And Wash Up 1 Mechanical Plan | FS1018-PIN-ZZ-00-D-O-7301
FS1018-PIN-ZZ-00-D-O-7401 | Food Prep Area, Kitchen Servery And Wash Up 1 Mechanical Elevations | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-02 | 1. Pinnacle services are not in the correct location, refer to AGL Services drawings and are clashing with the doorway. 2. AGL Services are required to be extended to new sink location 3 AGL Services are required to be adjusted to new sink location 4. Unit clash with doorway 5. Misspelling of tundish 6. There is no drinking water, cold water is from a boosted cold water system, see AGL drawings 7. How is grease managed? If there is a grease trap, who is supplying the grease trap? | TRUE | FS1018-PIN-ZZ-00-D-O-7401 Food Prep Area, Kitchen Servery And Wash Up 1 Mechanical Elevations | FS1018-PIN-ZZ-00-D-O-7401
FS1018-PIN-ZZ-00-D-O-7401 | Food Prep Area, Kitchen Servery And Wash Up 1 Mechanical Elevations | P03 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-7401 Food Prep Area, Kitchen Servery And Wash Up 1 Mechanical Elevations | FS1018-PIN-ZZ-00-D-O-7401
FS1018-PIN-ZZ-00-D-O-7501 | Dishwash Services Requirements | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-04-02 | 1.AGL services are to be adjusted to suite new unit locations 2.How is grease managed? If there is a grease trap, who is supplying the grease trap? Dishwasher and combi ovens 3.Floor gully (G), who is positioning the gully? AGL or Pinnacle? Table clashing with gully | TRUE | FS1018-PIN-ZZ-00-D-O-7501 Dishwash Services Requirements | FS1018-PIN-ZZ-00-D-O-7501
FS1018-PIN-ZZ-00-D-O-7501 | Dishwash Services Requirements | P03 | In Progress | 2025-04-02 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-7501 Dishwash Services Requirements | FS1018-PIN-ZZ-00-D-O-7501
FS1018-PIN-ZZ-00-D-O-8001 | Music Practice Room 1 | P04 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-00-D-O-8001 Music Practice Room 1 | FS1018-PIN-ZZ-00-D-O-8001
FS1018-PIN-ZZ-00-D-O-8003 | Music Practice Room Extensive 1 | P04 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-00-D-O-8003 Music Practice Room Extensive 1 | FS1018-PIN-ZZ-00-D-O-8003
FS1018-PIN-ZZ-00-D-O-9001 | Classroom Store, Room Off Sen Room 1 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | SOA is 5m2, 3.28m2 provided. | TRUE | FS1018-PIN-ZZ-00-D-O-9001 Classroom Store, Room Off Sen Room 1 | FS1018-PIN-ZZ-00-D-O-9001
FS1018-PIN-ZZ-00-D-O-9001 | Classroom Store, Room Off Sen Room 1 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-00-D-O-9001 Classroom Store, Room Off Sen Room 1 | FS1018-PIN-ZZ-00-D-O-9001
FS1018-PIN-ZZ-00-D-O-9003 | Teaching Resources Store Music 2 | P03 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-00-D-O-9003 Teaching Resources Store Music 2 | FS1018-PIN-ZZ-00-D-O-9003
FS1018-PIN-ZZ-01-D-O-1000 | First Floor GA 1 Of 2 | P05 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-01-D-O-1000 First Floor GA 1 Of 2 | FS1018-PIN-ZZ-01-D-O-1000
FS1018-PIN-ZZ-01-D-O-1000 | First Floor GA 1 Of 2 | P05 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-01-D-O-1000 First Floor GA 1 Of 2 | FS1018-PIN-ZZ-01-D-O-1000
FS1018-PIN-ZZ-01-D-O-1001 | First Floor GA 2 Of 2 | P05 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Update based on review comments. 2. Is water fountain would be better located between office and SEN room? | TRUE | FS1018-PIN-ZZ-01-D-O-1001 First Floor GA 2 Of 2 | FS1018-PIN-ZZ-01-D-O-1001
FS1018-PIN-ZZ-01-D-O-1001 | First Floor GA 2 Of 2 | P05 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-01-D-O-1001 First Floor GA 2 Of 2 | FS1018-PIN-ZZ-01-D-O-1001
FS1018-PIN-ZZ-01-D-O-1002 | Classroom General 2 | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | No DDA desk shown. Add desk spacing dims. | TRUE | FS1018-PIN-ZZ-01-D-O-1002 Classroom General 2 | FS1018-PIN-ZZ-01-D-O-1002
FS1018-PIN-ZZ-01-D-O-1002 | Classroom General 2 | P04 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-01-D-O-1002 Classroom General 2 | FS1018-PIN-ZZ-01-D-O-1002
FS1018-PIN-ZZ-01-D-O-1003 | Classroom General 3 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | No DDA desk shown. Add desk spacing dims. | TRUE | FS1018-PIN-ZZ-01-D-O-1003 Classroom General 3 | FS1018-PIN-ZZ-01-D-O-1003
FS1018-PIN-ZZ-01-D-O-1003 | Classroom General 3 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-01-D-O-1003 Classroom General 3 | FS1018-PIN-ZZ-01-D-O-1003
FS1018-PIN-ZZ-01-D-O-1004 | Classroom General 4 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Add desk spacing dims. | TRUE | FS1018-PIN-ZZ-01-D-O-1004 Classroom General 4 | FS1018-PIN-ZZ-01-D-O-1004
FS1018-PIN-ZZ-01-D-O-1004 | Classroom General 4 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-01-D-O-1004 Classroom General 4 | FS1018-PIN-ZZ-01-D-O-1004
FS1018-PIN-ZZ-01-D-O-1005 | Classroom General 5 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | No DDA desk shown. Add desk spacing dims. | TRUE | FS1018-PIN-ZZ-01-D-O-1005 Classroom General 5 | FS1018-PIN-ZZ-01-D-O-1005
FS1018-PIN-ZZ-01-D-O-1005 | Classroom General 5 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-01-D-O-1005 Classroom General 5 | FS1018-PIN-ZZ-01-D-O-1005
FS1018-PIN-ZZ-01-D-O-1006 | Classroom General 6 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | No DDA desk shown. Add desk spacing dims. | TRUE | FS1018-PIN-ZZ-01-D-O-1006 Classroom General 6 | FS1018-PIN-ZZ-01-D-O-1006
FS1018-PIN-ZZ-01-D-O-1006 | Classroom General 6 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-01-D-O-1006 Classroom General 6 | FS1018-PIN-ZZ-01-D-O-1006
FS1018-PIN-ZZ-01-D-O-1007 | Classroom General 7 | P05 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Add desk spacing dims. | TRUE | FS1018-PIN-ZZ-01-D-O-1007 Classroom General 7 | FS1018-PIN-ZZ-01-D-O-1007
FS1018-PIN-ZZ-01-D-O-1007 | Classroom General 7 | P05 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-01-D-O-1007 Classroom General 7 | FS1018-PIN-ZZ-01-D-O-1007
FS1018-PIN-ZZ-01-D-O-1008 | Classroom General 8 | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | No DDA desk shown. Add desk spacing dims. | TRUE | FS1018-PIN-ZZ-01-D-O-1008 Classroom General 8 | FS1018-PIN-ZZ-01-D-O-1008
FS1018-PIN-ZZ-01-D-O-1008 | Classroom General 8 | P04 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-01-D-O-1008 Classroom General 8 | FS1018-PIN-ZZ-01-D-O-1008
FS1018-PIN-ZZ-01-D-O-1009 | Classroom General 9 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | No DDA desk shown. Add desk spacing dims. . | TRUE | FS1018-PIN-ZZ-01-D-O-1009 Classroom General 9 | FS1018-PIN-ZZ-01-D-O-1009
FS1018-PIN-ZZ-01-D-O-1009 | Classroom General 9 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-01-D-O-1009 Classroom General 9 | FS1018-PIN-ZZ-01-D-O-1009
FS1018-PIN-ZZ-01-D-O-1021 | Classroom General 1 | P05 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Add desk spacing dims. | TRUE | FS1018-PIN-ZZ-01-D-O-1021 Classroom General 1 | FS1018-PIN-ZZ-01-D-O-1021
FS1018-PIN-ZZ-01-D-O-1021 | Classroom General 1 | P05 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-01-D-O-1021 Classroom General 1 | FS1018-PIN-ZZ-01-D-O-1021
FS1018-PIN-ZZ-01-D-O-1101 | ICT Rich Classroom 1 | P06 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Can the middle bank of desk be moved 200cm towards the door to allow for better circulation? | TRUE | FS1018-PIN-ZZ-01-D-O-1101 ICT Rich Classroom 1 | FS1018-PIN-ZZ-01-D-O-1101
FS1018-PIN-ZZ-01-D-O-1101 | ICT Rich Classroom 1 | P06 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-01-D-O-1101 ICT Rich Classroom 1 | FS1018-PIN-ZZ-01-D-O-1101
FS1018-PIN-ZZ-01-D-O-1102 | ICT Rich Classroom 2 | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Can you relocate the DDA desk to the centre bank of desk, so they do not have their back to the whiteboard? 2.Can you rotate the teacher's desk to face door? | TRUE | FS1018-PIN-ZZ-01-D-O-1102 ICT Rich Classroom 2 | FS1018-PIN-ZZ-01-D-O-1102
FS1018-PIN-ZZ-01-D-O-1102 | ICT Rich Classroom 2 | P04 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-01-D-O-1102 ICT Rich Classroom 2 | FS1018-PIN-ZZ-01-D-O-1102
FS1018-PIN-ZZ-01-D-O-1108 | Art Room General | P05 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-01-D-O-1108 Art Room General | FS1018-PIN-ZZ-01-D-O-1108
FS1018-PIN-ZZ-01-D-O-3006 | Medical Treatment Mi Room 1 And 3007 Sen Resource Space 1 | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Not ideal to access medical room off the SEN room, potential switch with staff workroom? | TRUE | FS1018-PIN-ZZ-01-D-O-3006 Medical Treatment Mi Room 1 And 3007 Sen Resource Space 1 | FS1018-PIN-ZZ-01-D-O-3006
FS1018-PIN-ZZ-01-D-O-3006 | Medical Treatment Mi Room 1 And 3007 Sen Resource Space 1 | P04 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-01-D-O-3006 Medical Treatment Mi Room 1 And 3007 Sen Resource Space 1 | FS1018-PIN-ZZ-01-D-O-3006
FS1018-PIN-ZZ-01-D-O-3009 | Small Group Room Large Sen Etc. 1 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Can DAA desk be moved to the other end of the desk bank and dimensions added to demonstrate adequate circulation is provided | TRUE | FS1018-PIN-ZZ-01-D-O-3009 Small Group Room Large Sen Etc. 1 | FS1018-PIN-ZZ-01-D-O-3009
FS1018-PIN-ZZ-01-D-O-3009 | Small Group Room Large Sen Etc. 1 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-01-D-O-3009 Small Group Room Large Sen Etc. 1 | FS1018-PIN-ZZ-01-D-O-3009
FS1018-PIN-ZZ-01-D-O-4002 | Meeting Room Conference 1 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1. What is proposed occupancy? Is the room area too large for the requirements or is the FF&E provision too little. | TRUE | FS1018-PIN-ZZ-01-D-O-4002 Meeting Room Conference 1 | FS1018-PIN-ZZ-01-D-O-4002
FS1018-PIN-ZZ-01-D-O-4002 | Meeting Room Conference 1 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-01-D-O-4002 Meeting Room Conference 1 | FS1018-PIN-ZZ-01-D-O-4002
FS1018-PIN-ZZ-01-D-O-4007 | Office Pastoral 1 And 5002 Teaching Resources Store It Gt Off Corridor 2 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Is this the most appropriate layout, tall shelving near the window, I think a better layout can be achieved. | TRUE | FS1018-PIN-ZZ-01-D-O-4007 Office Pastoral 1 And 5002 Teaching Resources Store It Gt Off Corridor 2 | FS1018-PIN-ZZ-01-D-O-4007
FS1018-PIN-ZZ-01-D-O-4007 | Office Pastoral 1 And 5002 Teaching Resources Store It Gt Off Corridor 2 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-01-D-O-4007 Office Pastoral 1 And 5002 Teaching Resources Store It Gt Off Corridor 2 | FS1018-PIN-ZZ-01-D-O-4007
FS1018-PIN-ZZ-01-D-O-4012 | Office With Meeting Area, 2 Person 1 | P04 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-01-D-O-4012 Office With Meeting Area, 2 Person 1 | FS1018-PIN-ZZ-01-D-O-4012
FS1018-PIN-ZZ-01-D-O-4013 | Office With Meeting Area, 2 Person 2 | P04 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-01-D-O-4013 Office With Meeting Area, 2 Person 2 | FS1018-PIN-ZZ-01-D-O-4013
FS1018-PIN-ZZ-01-D-O-4016 | Office Senco, Learning Support 1 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Can the layout of the this room with the classroom store near the window be improved? | TRUE | FS1018-PIN-ZZ-01-D-O-4016 Office Senco, Learning Support 1 | FS1018-PIN-ZZ-01-D-O-4016
FS1018-PIN-ZZ-01-D-O-4016 | Office Senco, Learning Support 1 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-01-D-O-4016 Office Senco, Learning Support 1 | FS1018-PIN-ZZ-01-D-O-4016
FS1018-PIN-ZZ-01-D-O-4017 | Staff Workroom ICT Technicians 1 | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Tambour unit is against a window | TRUE | FS1018-PIN-ZZ-01-D-O-4017 Staff Workroom ICT Technicians 1 | FS1018-PIN-ZZ-01-D-O-4017
FS1018-PIN-ZZ-01-D-O-4017 | Staff Workroom ICT Technicians 1 | P02 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-01-D-O-4017 Staff Workroom ICT Technicians 1 | FS1018-PIN-ZZ-01-D-O-4017
FS1018-PIN-ZZ-01-D-O-5006 | Teaching Resources Store Off Art Room 1 | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-01-D-O-5006 Teaching Resources Store Off Art Room 1 | FS1018-PIN-ZZ-01-D-O-5006
FS1018-PIN-ZZ-01-D-O-5017 | Classroom Store, Room Off Sen Room 1 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Can the layout of the this room with the classroom store near the window be improved. Doesn't seem the most logical use of space and daylight. | TRUE | FS1018-PIN-ZZ-01-D-O-5017 Classroom Store, Room Off Sen Room 1 | FS1018-PIN-ZZ-01-D-O-5017
FS1018-PIN-ZZ-01-D-O-5017 | Classroom Store, Room Off Sen Room 1 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-01-D-O-5017 Classroom Store, Room Off Sen Room 1 | FS1018-PIN-ZZ-01-D-O-5017
FS1018-PIN-ZZ-01-D-O-5104 | Secure Storeroom 2 | P03 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-01-D-O-5104 Secure Storeroom 2 | FS1018-PIN-ZZ-01-D-O-5104
FS1018-PIN-ZZ-01-D-O-5110 | Coats And Bag Store Lockers 2 | P03 | In Progress | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Appreciate the trust has specifically removed these. Please indicate on each locker drawing the location of the lockers and quantity of lockers that could be provided in that area if later required, with the overall number of lockers also listed for reference. | TRUE | FS1018-PIN-ZZ-01-D-O-5110 Coats And Bag Store Lockers 2 | FS1018-PIN-ZZ-01-D-O-5110
FS1018-PIN-ZZ-01-D-O-5110 | Coats And Bag Store Lockers 2 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-01-D-O-5110 Coats And Bag Store Lockers 2 | FS1018-PIN-ZZ-01-D-O-5110
FS1018-PIN-ZZ-01-D-O-5111 | Coats And Bag Store Lockers 3 | P03 | In Progress | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Appreciate the trust has specifically removed these. Please indicate on each locker drawing the location of the lockers and quantity of lockers that could be provided in that area if later required, with the overall number of lockers also listed for reference. | TRUE | FS1018-PIN-ZZ-01-D-O-5111 Coats And Bag Store Lockers 3 | FS1018-PIN-ZZ-01-D-O-5111
FS1018-PIN-ZZ-01-D-O-5111 | Coats And Bag Store Lockers 3 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-01-D-O-5111 Coats And Bag Store Lockers 3 | FS1018-PIN-ZZ-01-D-O-5111
FS1018-PIN-ZZ-01-D-O-5112 | Coats And Bag Store Lockers 4 | P03 | In Progress | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Appreciate the trust has specifically removed these. Please indicate on each locker drawing the location of the lockers and quantity of lockers that could be provided in that area if later required, with the overall number of lockers also listed for reference. | TRUE | FS1018-PIN-ZZ-01-D-O-5112 Coats And Bag Store Lockers 4 | FS1018-PIN-ZZ-01-D-O-5112
FS1018-PIN-ZZ-01-D-O-5112 | Coats And Bag Store Lockers 4 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-01-D-O-5112 Coats And Bag Store Lockers 4 | FS1018-PIN-ZZ-01-D-O-5112
FS1018-PIN-ZZ-01-D-O-5113 | Coats And Bag Store Lockers 5 | P03 | In Progress | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Appreciate the trust has specifically removed these. Please indicate on each locker drawing the location of the lockers and quantity of lockers that could be provided in that area if later required, with the overall number of lockers also listed for reference. | TRUE | FS1018-PIN-ZZ-01-D-O-5113 Coats And Bag Store Lockers 5 | FS1018-PIN-ZZ-01-D-O-5113
FS1018-PIN-ZZ-01-D-O-5113 | Coats And Bag Store Lockers 5 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-01-D-O-5113 Coats And Bag Store Lockers 5 | FS1018-PIN-ZZ-01-D-O-5113
FS1018-PIN-ZZ-01-D-O-5116 | Cleaners' Store 3 | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-01-D-O-5116 Cleaners' Store 3 | FS1018-PIN-ZZ-01-D-O-5116
FS1018-PIN-ZZ-02-D-O-1010 | Classroom General 10 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Add desk spacing dims. | TRUE | FS1018-PIN-ZZ-02-D-O-1010 Classroom General 10 | FS1018-PIN-ZZ-02-D-O-1010
FS1018-PIN-ZZ-02-D-O-1010 | Classroom General 10 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-02-D-O-1010 Classroom General 10 | FS1018-PIN-ZZ-02-D-O-1010
FS1018-PIN-ZZ-02-D-O-1011 | Classroom General 11 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | No DDA desk shown. Add desk spacing dims. | TRUE | FS1018-PIN-ZZ-02-D-O-1011 Classroom General 11 | FS1018-PIN-ZZ-02-D-O-1011
FS1018-PIN-ZZ-02-D-O-1011 | Classroom General 11 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-02-D-O-1011 Classroom General 11 | FS1018-PIN-ZZ-02-D-O-1011
FS1018-PIN-ZZ-02-D-O-1012 | Classroom General 12 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | No DDA desk shown. Add desk spacing dims. | TRUE | FS1018-PIN-ZZ-02-D-O-1012 Classroom General 12 | FS1018-PIN-ZZ-02-D-O-1012
FS1018-PIN-ZZ-02-D-O-1012 | Classroom General 12 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-02-D-O-1012 Classroom General 12 | FS1018-PIN-ZZ-02-D-O-1012
FS1018-PIN-ZZ-02-D-O-1013 | Classroom General 13 | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | No DDA desk shown. Add desk spacing dims. | TRUE | FS1018-PIN-ZZ-02-D-O-1013 Classroom General 13 | FS1018-PIN-ZZ-02-D-O-1013
FS1018-PIN-ZZ-02-D-O-1013 | Classroom General 13 | P04 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-02-D-O-1013 Classroom General 13 | FS1018-PIN-ZZ-02-D-O-1013
FS1018-PIN-ZZ-02-D-O-1014 | Classroom General 14 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Add desk spacing dims. | TRUE | FS1018-PIN-ZZ-02-D-O-1014 Classroom General 14 | FS1018-PIN-ZZ-02-D-O-1014
FS1018-PIN-ZZ-02-D-O-1014 | Classroom General 14 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-02-D-O-1014 Classroom General 14 | FS1018-PIN-ZZ-02-D-O-1014
FS1018-PIN-ZZ-02-D-O-1015 | Classroom General 15 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | No DDA desk shown. Add desk spacing dims. | TRUE | FS1018-PIN-ZZ-02-D-O-1015 Classroom General 15 | FS1018-PIN-ZZ-02-D-O-1015
FS1018-PIN-ZZ-02-D-O-1015 | Classroom General 15 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-02-D-O-1015 Classroom General 15 | FS1018-PIN-ZZ-02-D-O-1015
FS1018-PIN-ZZ-02-D-O-1016 | Classroom General 16 | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Add desk spacing dims. | TRUE | FS1018-PIN-ZZ-02-D-O-1016 Classroom General 16 | FS1018-PIN-ZZ-02-D-O-1016
FS1018-PIN-ZZ-02-D-O-1016 | Classroom General 16 | P04 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-02-D-O-1016 Classroom General 16 | FS1018-PIN-ZZ-02-D-O-1016
FS1018-PIN-ZZ-02-D-O-1042 | 6042P Stairway 7 And 5113A Coats And Bag Store Lockers 5 | P03 | In Progress | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Appreciate the trust has specifically removed these. Please indicate on each locker drawing the location of the lockers and quantity of lockers that could be provided in that area if later required, with the overall number of lockers also listed for reference. | TRUE | FS1018-PIN-ZZ-02-D-O-1042 6042P Stairway 7 And 5113A Coats And Bag Store Lockers 5 | FS1018-PIN-ZZ-02-D-O-1042
FS1018-PIN-ZZ-02-D-O-1042 | 6042P Stairway 7 And 5113A Coats And Bag Store Lockers 5 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-02-D-O-1042 6042P Stairway 7 And 5113A Coats And Bag Store Lockers 5 | FS1018-PIN-ZZ-02-D-O-1042
FS1018-PIN-ZZ-02-D-O-1103 | Science Laboratories Restrictive, Extg 1 | P05 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | No DDA desk shown. Add desk spacing dims. | TRUE | FS1018-PIN-ZZ-02-D-O-1103 Science Laboratories Restrictive, Extg 1 | FS1018-PIN-ZZ-02-D-O-1103
FS1018-PIN-ZZ-02-D-O-1103 | Science Laboratories Restrictive, Extg 1 | P05 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-02-D-O-1103 Science Laboratories Restrictive, Extg 1 | FS1018-PIN-ZZ-02-D-O-1103
FS1018-PIN-ZZ-02-D-O-1104 | Science Laboratories Restrictive, Extg 2 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | No DDA desk shown. Add desk spacing dims. | TRUE | FS1018-PIN-ZZ-02-D-O-1104 Science Laboratories Restrictive, Extg 2 | FS1018-PIN-ZZ-02-D-O-1104
FS1018-PIN-ZZ-02-D-O-1104 | Science Laboratories Restrictive, Extg 2 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-02-D-O-1104 Science Laboratories Restrictive, Extg 2 | FS1018-PIN-ZZ-02-D-O-1104
FS1018-PIN-ZZ-02-D-O-1105 | Science Laboratories Restrictive, Extg 3 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Can DDA face the whiteboard. Add desk spacing dims. | TRUE | FS1018-PIN-ZZ-02-D-O-1105 Science Laboratories Restrictive, Extg 3 | FS1018-PIN-ZZ-02-D-O-1105
FS1018-PIN-ZZ-02-D-O-1105 | Science Laboratories Restrictive, Extg 3 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-02-D-O-1105 Science Laboratories Restrictive, Extg 3 | FS1018-PIN-ZZ-02-D-O-1105
FS1018-PIN-ZZ-02-D-O-1106 | Science Laboratories Restrictive, Extg 4 | P04 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Add desk spacing dims. | TRUE | FS1018-PIN-ZZ-02-D-O-1106 Science Laboratories Restrictive, Extg 4 | FS1018-PIN-ZZ-02-D-O-1106
FS1018-PIN-ZZ-02-D-O-1106 | Science Laboratories Restrictive, Extg 4 | P04 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-02-D-O-1106 Science Laboratories Restrictive, Extg 4 | FS1018-PIN-ZZ-02-D-O-1106
FS1018-PIN-ZZ-02-D-O-1107 | Science Laboratories Restrictive, Extg 5 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Can DDA face the whiteboard. Add desk spacing dims. | TRUE | FS1018-PIN-ZZ-02-D-O-1107 Science Laboratories Restrictive, Extg 5 | FS1018-PIN-ZZ-02-D-O-1107
FS1018-PIN-ZZ-02-D-O-1107 | Science Laboratories Restrictive, Extg 5 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-02-D-O-1107 Science Laboratories Restrictive, Extg 5 | FS1018-PIN-ZZ-02-D-O-1107
FS1018-PIN-ZZ-02-D-O-2000 | Second Floor GA | P05 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Update based on comments 2. Is the water fountain the best location near busy door ways, can this be located near the office with less traffic. Office door be more centrally placed. | TRUE | FS1018-PIN-ZZ-02-D-O-2000 Second Floor GA | FS1018-PIN-ZZ-02-D-O-2000
FS1018-PIN-ZZ-02-D-O-2000 | Second Floor GA | P05 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-02-D-O-2000 Second Floor GA | FS1018-PIN-ZZ-02-D-O-2000
FS1018-PIN-ZZ-02-D-O-2042 | 6042O Stairway 7 And 5113B Coats And Bag Store Lockers 5 | P03 | In Progress | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Appreciate the trust has specifically removed these. Please indicate on each locker drawing the location of the lockers and quantity of lockers that could be provided in that area if later required, with the overall number of lockers also listed for reference. | TRUE | FS1018-PIN-ZZ-02-D-O-2042 6042O Stairway 7 And 5113B Coats And Bag Store Lockers 5 | FS1018-PIN-ZZ-02-D-O-2042
FS1018-PIN-ZZ-02-D-O-2042 | 6042O Stairway 7 And 5113B Coats And Bag Store Lockers 5 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-02-D-O-2042 6042O Stairway 7 And 5113B Coats And Bag Store Lockers 5 | FS1018-PIN-ZZ-02-D-O-2042
FS1018-PIN-ZZ-02-D-O-3008 | Small Group Room Medium 1 And 6042T Stairway 7 | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Should seating for 6 puplils be provided not 2.Add desk spacing dims | TRUE | FS1018-PIN-ZZ-02-D-O-3008 Small Group Room Medium 1 And 6042T Stairway 7 | FS1018-PIN-ZZ-02-D-O-3008
FS1018-PIN-ZZ-02-D-O-3008 | Small Group Room Medium 1 And 6042T Stairway 7 | P02 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-02-D-O-3008 Small Group Room Medium 1 And 6042T Stairway 7 | FS1018-PIN-ZZ-02-D-O-3008
FS1018-PIN-ZZ-02-D-O-3042 | 6042N Stairway 7, 5113C And 5113D Coats And Bag Store Lockers 5 | P03 | In Progress | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Appreciate the trust has specifically removed these. Please indicate on each locker drawing the location of the lockers and quantity of lockers that could be provided in that area if later required, with the overall number of lockers also listed for reference. | TRUE | FS1018-PIN-ZZ-02-D-O-3042 6042N Stairway 7, 5113C And 5113D Coats And Bag Store Lockers 5 | FS1018-PIN-ZZ-02-D-O-3042
FS1018-PIN-ZZ-02-D-O-3042 | 6042N Stairway 7, 5113C And 5113D Coats And Bag Store Lockers 5 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-02-D-O-3042 6042N Stairway 7, 5113C And 5113D Coats And Bag Store Lockers 5 | FS1018-PIN-ZZ-02-D-O-3042
FS1018-PIN-ZZ-02-D-O-4001 | Staff Workroom Teaching Staff 1 And Teaching Resources Store It Gt Off Corridor 3 | P05 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | 1.Floating shelving units in the middle of the room away from wall, can a better solution be found. | TRUE | FS1018-PIN-ZZ-02-D-O-4001 Staff Workroom Teaching Staff 1 And Teaching Resources Store It Gt Off Corridor 3 | FS1018-PIN-ZZ-02-D-O-4001
FS1018-PIN-ZZ-02-D-O-4001 | Staff Workroom Teaching Staff 1 And Teaching Resources Store It Gt Off Corridor 3 | P05 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-02-D-O-4001 Staff Workroom Teaching Staff 1 And Teaching Resources Store It Gt Off Corridor 3 | FS1018-PIN-ZZ-02-D-O-4001
FS1018-PIN-ZZ-02-D-O-4014 | Office With Meeting Area, 2 Person 3 | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Add desk spacing dims. | TRUE | FS1018-PIN-ZZ-02-D-O-4014 Office With Meeting Area, 2 Person 3 | FS1018-PIN-ZZ-02-D-O-4014
FS1018-PIN-ZZ-02-D-O-4014 | Office With Meeting Area, 2 Person 3 | P02 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-02-D-O-4014 Office With Meeting Area, 2 Person 3 | FS1018-PIN-ZZ-02-D-O-4014
FS1018-PIN-ZZ-02-D-O-5004 | Science Prep Option 1 | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Iso & elevations do not match plan. | TRUE | FS1018-PIN-ZZ-02-D-O-5004 Science Prep Option 1 | FS1018-PIN-ZZ-02-D-O-5004
FS1018-PIN-ZZ-02-D-O-5004 | Science Prep Option 1 | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-02-D-O-5004 Science Prep Option 1 | FS1018-PIN-ZZ-02-D-O-5004
FS1018-PIN-ZZ-02-D-O-5005 | Chemical Store 1 | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-02-D-O-5005 Chemical Store 1 | FS1018-PIN-ZZ-02-D-O-5005
FS1018-PIN-ZZ-02-D-O-5020 | Science Prep | P03 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Is the fume cupboard located in the best location, limited circulation. | TRUE | FS1018-PIN-ZZ-02-D-O-5020 Science Prep | FS1018-PIN-ZZ-02-D-O-5020
FS1018-PIN-ZZ-02-D-O-5020 | Science Prep | P03 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-02-D-O-5020 Science Prep | FS1018-PIN-ZZ-02-D-O-5020
FS1018-PIN-ZZ-02-D-O-5102 | General Storeroom Central Stock 1 | P02 | Completed | 2025-03-13 | DFE Review | A - Accepted | 2025-03-31 |  | TRUE | FS1018-PIN-ZZ-02-D-O-5102 General Storeroom Central Stock 1 | FS1018-PIN-ZZ-02-D-O-5102
FS1018-PIN-ZZ-02-D-O-5115 | Cleaners' Store 2 | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | Door opening does not reflect GA plans, which is correct? | TRUE | FS1018-PIN-ZZ-02-D-O-5115 Cleaners' Store 2 | FS1018-PIN-ZZ-02-D-O-5115
FS1018-PIN-ZZ-02-D-O-5115 | Cleaners' Store 2 | P02 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-02-D-O-5115 Cleaners' Store 2 | FS1018-PIN-ZZ-02-D-O-5115
FS1018-PIN-ZZ-02-D-O-6113 | Coats And Bags Store Lockers 5 | P02 | In Progress | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Appreciate the trust has specifically removed these. Please indicate on each locker drawing the location of the lockers and quantity of lockers that could be provided in that area if later required, with the overall number of lockers also listed for reference. | TRUE | FS1018-PIN-ZZ-02-D-O-6113 Coats And Bags Store Lockers 5 | FS1018-PIN-ZZ-02-D-O-6113
FS1018-PIN-ZZ-02-D-O-6113 | Coats And Bags Store Lockers 5 | P02 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-02-D-O-6113 Coats And Bags Store Lockers 5 | FS1018-PIN-ZZ-02-D-O-6113
FS1018-PIN-ZZ-02-D-O-7113 | Coats And Bags Store Lockers 5 | P02 | In Progress | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Appreciate the trust has specifically removed these. Please indicate on each locker drawing the location of the lockers and quantity of lockers that could be provided in that area if later required, with the overall number of lockers also listed for reference. | TRUE | FS1018-PIN-ZZ-02-D-O-7113 Coats And Bags Store Lockers 5 | FS1018-PIN-ZZ-02-D-O-7113
FS1018-PIN-ZZ-02-D-O-7113 | Coats And Bags Store Lockers 5 | P02 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-02-D-O-7113 Coats And Bags Store Lockers 5 | FS1018-PIN-ZZ-02-D-O-7113
FS1018-PIN-ZZ-02-D-O-8113 | Coats And Bags Store Lockers 5 | P02 | In Progress | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Appreciate the trust has specifically removed these. Please indicate on each locker drawing the location of the lockers and quantity of lockers that could be provided in that area if later required, with the overall number of lockers also listed for reference. | TRUE | FS1018-PIN-ZZ-02-D-O-8113 Coats And Bags Store Lockers 5 | FS1018-PIN-ZZ-02-D-O-8113
FS1018-PIN-ZZ-02-D-O-8113 | Coats And Bags Store Lockers 5 | P02 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-02-D-O-8113 Coats And Bags Store Lockers 5 | FS1018-PIN-ZZ-02-D-O-8113
FS1018-PIN-ZZ-02-D-O-9113 | Coats And Bags Store Lockers 5 | P02 | In Progress | 2025-03-13 | DFE Review | B - Partially Accepted with Comments | 2025-03-31 | Appreciate the trust has specifically removed these. Please indicate on each locker drawing the location of the lockers and quantity of lockers that could be provided in that area if later required, with the overall number of lockers also listed for reference. | TRUE | FS1018-PIN-ZZ-02-D-O-9113 Coats And Bags Store Lockers 5 | FS1018-PIN-ZZ-02-D-O-9113
FS1018-PIN-ZZ-02-D-O-9113 | Coats And Bags Store Lockers 5 | P02 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-02-D-O-9113 Coats And Bags Store Lockers 5 | FS1018-PIN-ZZ-02-D-O-9113
FS1018-PIN-ZZ-ZZ-L-O-0005 | FFE Gap Analysis and Occupancy Schedule | P02 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | To be updated based on review comments | TRUE | FS1018-PIN-ZZ-ZZ-L-O-0005 FFE Gap Analysis and Occupancy Schedule | FS1018-PIN-ZZ-ZZ-L-O-0005
FS1018-PIN-ZZ-ZZ-L-O-0005 | FFE Gap Analysis and Occupancy Schedule | P02 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-ZZ-L-O-0005 FFE Gap Analysis and Occupancy Schedule | FS1018-PIN-ZZ-ZZ-L-O-0005
FS1018-PIN-ZZ-ZZ-L-O-0006 | Catering Equipment Schedule | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | To be updated based on review comments | TRUE | FS1018-PIN-ZZ-ZZ-L-O-0006 Catering Equipment Schedule | FS1018-PIN-ZZ-ZZ-L-O-0006
FS1018-PIN-ZZ-ZZ-L-O-0006 | Catering Equipment Schedule | P01 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-ZZ-L-O-0006 Catering Equipment Schedule | FS1018-PIN-ZZ-ZZ-L-O-0006
FS1018-PIN-ZZ-ZZ-L-O-0007 | FFE Cost Plan | P01 | In Progress | 2025-03-13 | DFE Review | C - Rejected | 2025-03-31 | To be updated based on review comments | TRUE | FS1018-PIN-ZZ-ZZ-L-O-0007 FFE Cost Plan | FS1018-PIN-ZZ-ZZ-L-O-0007
FS1018-PIN-ZZ-ZZ-L-O-0007 | FFE Cost Plan | P01 | In Progress | 2025-03-31 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-ZZ-L-O-0007 FFE Cost Plan | FS1018-PIN-ZZ-ZZ-L-O-0007
FS1018-PIN-ZZ-ZZ-M-O-0001 | FFE Revit Model | P11 | In Progress | 2025-04-17 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-ZZ-M-O-0001 FFE Revit Model | FS1018-PIN-ZZ-ZZ-M-O-0001
FS1018-PIN-ZZ-ZZ-M-O-0001 | FFE Revit Model | P11 | In Progress | 2025-04-17 | DFE Review | C - Rejected | 2025-04-17 | Model Number is incorrect in the Splash sheet. Level 01is not displaying in model | TRUE | FS1018-PIN-ZZ-ZZ-M-O-0001 FFE Revit Model | FS1018-PIN-ZZ-ZZ-M-O-0001
FS1018-PIN-ZZ-ZZ-M-O-0002 | FFE IFC Model | P09 | Completed | 2025-04-09 | DFE Review | A - Accepted | 2025-04-16 |  | TRUE | FS1018-PIN-ZZ-ZZ-M-O-0002 FFE IFC Model | FS1018-PIN-ZZ-ZZ-M-O-0002
FS1018-PIN-ZZ-ZZ-M-O-0002 | FFE IFC Model | P09 | In Progress | 2025-04-17 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-ZZ-M-O-0002 FFE IFC Model | FS1018-PIN-ZZ-ZZ-M-O-0002
FS1018-PIN-ZZ-ZZ-M-O-0002 | FFE IFC Model | P09 | In Progress | 2025-04-17 | DFE Review | C - Rejected | 2025-04-17 | Not matching native model only level 00 displaying. | TRUE | FS1018-PIN-ZZ-ZZ-M-O-0002 FFE IFC Model | FS1018-PIN-ZZ-ZZ-M-O-0002
FS1018-PIN-ZZ-ZZ-M-O-0003 | FFE Navis Model | P07 | Completed | 2025-04-09 | DFE Review | A - Accepted | 2025-04-16 |  | TRUE | FS1018-PIN-ZZ-ZZ-M-O-0003 FFE Navis Model | FS1018-PIN-ZZ-ZZ-M-O-0003
FS1018-PIN-ZZ-ZZ-M-O-0003 | FFE Navis Model | P07 | Completed | 2025-04-17 | DFE Review | A - Accepted | 2025-04-17 |  | TRUE | FS1018-PIN-ZZ-ZZ-M-O-0003 FFE Navis Model | FS1018-PIN-ZZ-ZZ-M-O-0003
FS1018-PIN-ZZ-ZZ-M-O-0004 | Catering IFC Model | P03 | Completed | 2025-04-09 | DFE Review | A - Accepted | 2025-04-16 |  | TRUE | FS1018-PIN-ZZ-ZZ-M-O-0004 Catering IFC Model | FS1018-PIN-ZZ-ZZ-M-O-0004
FS1018-PIN-ZZ-ZZ-M-O-0005 | Catering Revit Model | P03 | In Progress | 2025-04-09 | DFE Review | C - Rejected | 2025-04-16 | Drawing number and revision on splash sheet not matching submission | TRUE | FS1018-PIN-ZZ-ZZ-M-O-0005 Catering Revit Model | FS1018-PIN-ZZ-ZZ-M-O-0005
FS1018-PIN-ZZ-ZZ-M-O-0005 | Catering Revit Model | P03 | In Progress | 2025-04-16 | Designer Response | Pending |  |  | TRUE | FS1018-PIN-ZZ-ZZ-M-O-0005 Catering Revit Model | FS1018-PIN-ZZ-ZZ-M-O-0005
FS1018-PIN-ZZ-ZZ-M-O-0006 | CATERING NWC MODEL | P02 | Completed | 2025-04-09 | DFE Review | A - Accepted | 2025-04-16 |  | TRUE | FS1018-PIN-ZZ-ZZ-M-O-0006 CATERING NWC MODEL | FS1018-PIN-ZZ-ZZ-M-O-0006