## Summary
Originally From | (All) | RFI Tracker
Client RFI | (All) | Project Name: MTP | Total number of RFIs: 127
Date Generated: 27/03/2026 14:36
Row Labels | Count of Status | Summary Page
Closed-Out | 16
Outstanding | 30
Overdue | 9
Responded | 72
Grand Total | 127

## Tracker
RFI Tracker
Project Name: MTP
Date Generated: 27/03/2026 14:36
Client RFI | (All)
RFI Status | (All)
Discipline(s) | (All)
| Date RFI Sent | RFI Description | RFI Response | Date RFI Responded | Latest Correspondence
AGL-SUBRFI-000001: DNO Approval
Responded | 2026-03-04 15:26 | Has DNO approval been sought for the increased demand on the building? If so please share correspondence. | Please see the attached the DNO quotation for upgrade | 2026-03-13 08:48 | HBC-RTSCRFI-000023
AGL-SUBRFI-000002: Missing Supplies
Responded | 2026-03-04 15:27 | Many distribution boards and supplies on the LV schematics can not be located on either the small power drawings or containment drawings, the cable references for the missing supplies are as below: - 06 -09 - 22 - 23 - 28 - 29 - 35 - 36 - 37 - 50 - 51 Please provide details of the locations of the above equipment. | Isolator for Cable Ref 6 - Device required between Gridlines A20-E20 to be sited to suit specialist equipment suppliers requirements. Isolator for Cable Ref 9 - Device shown between Gridlines E14-F14 to be sited to suit specialist equipment suppliers requirements. Isolator for Cable Refs 22/23 - 1No. Device shown between Gridlines K20-L20 to serve 1No. AS08 to be sited to suit specialist equipment suppliers requirements. Isolators for Cable Refs 28/29 - 2No. Devices (AS16/01 & AS16/02) shown between Gridlines G20-H20 to be sited to suit specialist equipment suppliers requirements. Isolators for Cable Refs 35/36 - Devices required between Gridlines D14-G14 to be sited to suit specialist equipment suppliers requirements. DB for Cable Ref 37 - Dis Board to be sited adjacent to UPS Isolators for Cable Refs 50/51 - Devices no longer required for Stage 3 design. | 2026-03-16 08:06 | HBC-RTSCRFI-000032
AGL-SUBRFI-000003: Missing Document
Responded | 2026-03-04 15:28 | In the data section of specification drawing 200SF4-WBS-ZZ-GF-DR-E-61299 is referred to, this drawing is not available on Aconex - please could you provide? | Please see attached from tender (not part of stage 3 pack) | 2026-03-11 15:50 | HBC-RTSCRFI-000010
AGL-SUBRFI-000004: Asset Register & Maximum Demand
Responded | 2026-03-04 15:28 | Please provide separate copies/files for the asset register and maximum demand spreadsheet, the versions appended to the specification are difficult to read due to low resolution on the document. | Copy of the Asset register as included within specification, Contractor to refer to latest MTC/Client information for equipment details to suit Stage 4 design requirements. Stage 3 Preliminary load assessment for information purposes, Contractor to develop their own as part of Stage 4 design works. | 2026-03-16 07:14 | HBC-RTSCRFI-000027
AGL-SUBRFI-000005: Data Network
Responded | 2026-03-05 08:09 | To enable the commencement of the containment sizing, please confirm which data outlets are served from comms 1 network and which are served from the comms 2 network? | Drawing MTC-SF4-DWG-10001 - SF4 Baseline Layout - B4.0 - Sheet 2of2 was used as the basis for the Stage 3 comms design. This drawing shall require revisiting with the MTC/Client's IT specialist as part of the Stage 4 design works to ensure comms outlet provisions are correctly captured. | 2026-03-16 07:47 | HBC-RTSCRFI-000028
AGL-SUBRFI-000006: Distribution Boards
Responded | 2026-03-10 15:55 | The schematics and drawings show a DB/WPK/P&L1 and a DB/WPK/P&L3 but no DB/WPK/P&L2? Is this a typing error? If not please advise where DB/WPK/P&L2 is located and what this serves? | The reference for Distribution Board DB/WPK/P&L2 was included within an earlier design iteration. The Board this reference used no longer features within the scheme. | 2026-03-16 07:48 | HBC-RTSCRFI-000029
AGL-SUBRFI-000007: AS03 Equipment
Responded | 2026-03-10 15:56 | On the electrical maximum demand sheet the AS03 is given a load of 173kW, but there is no supplies on the schematic or drawings attributed to AS03, and no information relating to AS03 in the asset register. Please can you provide further details on this equipment? | At the time of production of the preliminary Stage 3 Electrical Load Assessment, the requirements for the Breakout enclosure were still to be defined between gridlines C14-B18, therefore an allowance was used that can now be omitted from the Stage 4 design and the updated requirements used for this area instead. | 2026-03-16 07:48 | HBC-RTSCRFI-000030
AGL-SUBRFI-000008: Equipment for Future Use
Responded | 2026-03-10 15:56 | There are a number of large isolators on the small power drawings labelled 'allowance for future use', but no connections for this equipment shown on the schematics. Are these isolators to be supplied without a mains connection? These isolators are labelled 'FS', this is not in the abbrevatiations list, please confirm. | The 3No. Isolators between Gridlines T20-P20 were shown to provide future flexibility to the space at the time of producing the Stage 3 information, the MTC were unable to confirm if they were required. If the MTC/Client confirm they are required than they should be provided with a suitably rated LV connection back to SMP1. The abbreviation FS can be ignored, just Fuse Size, for which the proposed ratings are shown. | 2026-03-16 07:54 | HBC-RTSCRFI-000031
AGL-SUBRFI-000009: Equipment Required for Safe Shutdown
Outstanding | 2026-03-24 16:57 | Please confirm the strategy for safe shutdown of the facility from an electrical perspective. The following information is required: 1. Which breakers are to be open and which are to be closed in the event of power outage? i.e. which equipment is required to enable to the safe shutdown of the facility. 2. To programme the phased reconnection of the electrical loads on power failure, we require a list of supplies to be fed by the generator in order of priority. Please can you provide? 3. To enable the phased reconnection of electrical loads on power failure, we read the specification as requiring motorised breakers on the main switchboard (SB/SF4) only, all other breakers on sub-main panels will be standard, is this correct? | (blank) | (blank) | HBC-GC-000057
CPMG-SUBRFI-000001: CPMG RFI 1- Fire Report
Responded | 2026-02-25 10:35 | Please provide Fire Report/Strategy | Please see response from MTC: Fire Strategy will form part of the HAZZOP which is being developed by MTC representative. Fire Alarm Specialist contractor to develop strategy as part of RIBA Stage 4. | 2026-03-02 10:04 | HBC-RTSCRFI-000004
CPMG-SUBRFI-000002: CPMG RFI 2- Acoustic Report
Responded | 2026-02-25 10:51 | Please provide Acoustic report | An acoustic report for this project has not been produced | 2026-03-11 16:00 | FDG-RTRFI-000004
CPMG-SUBRFI-000003: CPMG RFI 3- Architectural Model
Responded | 2026-02-25 10:53 | We have reviewed the architectural model and it appears there are missing elements which include existing external wall and roof elements missing. Is this model correct or are there additional elements/models? | Revit model attached | 2026-03-12 14:29 | HBC-RTSCRFI-000017
CPMG-SUBRFI-000004: CPMG RFI 4- MTC Security Pack
Responded | 2026-02-25 10:54 | The architectural spec references a MTC security Pack regards to door hardware and security. Can this please be provided? | (blank) | (blank) | HBC-GC-000023
CPMG-SUBRFI-000005: CPMG RFI 5- Breakout enclosure
Responded | 2026-02-25 10:55 | Has the breakout/enclosure design/spec been confirmed? | Please refer to the structural information submitted | 2026-03-13 09:13 | HBC-RTSCRFI-000024
CPMG-SUBRFI-000006: CPMG RFI 6- Building Control
Responded | 2026-02-25 10:57 | Please provide an update on Building Control and the Full plans submission and if there are any implications to the issued Stage 3 information. | Plan checking fee paid by MTC and no further response from WBC | 2026-03-12 14:32 | HBC-RTSCRFI-000020
CPMG-SUBRFI-000007: CPMG RFI 7- Revit Models Coordinates
Responded | 2026-02-25 11:01 | Architectural and MEP model align to world coordinates. Structural model does not. Architectural and MEP Base point is N/S281555109 E/W 440737415. To GL A1. Please confirm this is what the team will be working to. Structural model will need to be updated to suit. | Watermans to update Revit Model | 2026-03-12 14:30 | HBC-GC-000036
CPMG-SUBRFI-000008: CPMG RFI 8- BEP
Responded | 2026-02-25 11:02 | Please provide the BEP | There is no BEP please see file naming document and SAL | 2026-03-11 15:41 | HBC-RTSCRFI-000008
CPMG-SUBRFI-000009: CPMG RFI 9- Remtech pentrations
Responded | 2026-02-25 11:03 | We understand the rooflight will be infilled with Remtech panels with ductwork penetrations. Is there a tested solution and typical details for fixings and penetrations developed to meet MTC requirements. | Please see correspondence and standard details from Remtech | 2026-03-12 17:24 | HBC-RTSCRFI-000022
CPMG-SUBRFI-000010: CPMG RFI 10- Document Naming Standards
Responded | 2026-02-25 11:04 | Is there a Document Naming Standards document? | Please see attached document that clarifies naming. Key points: - Project code & name : please use 'MTP' and no other information (i.e. no address), this helps to anonymise the project - All doc number codes as standard -Put security classification in filename | 2026-03-11 07:36 | HBC-RTSCRFI-000006
CPMG-SUBRFI-000011: CPMG RFI 11- Revit Models Coordinates
Responded | 2026-02-25 11:05 | Is there a Stage 3 federated model and clash detection report available? | There will be no federated model due to the sensitivity of the project | 2026-03-11 15:43 | HBC-RTSCRFI-000009
CPMG-SUBRFI-000012: CPMG RFI 12- Siphonic Drainage
Responded | 2026-02-25 11:09 | The architectural drawings and model reference siphonic drainage at high level. Can you please provide the siphonic drainage model or details. | The architectural model should contain the zone for the siphonic drainage. | 2026-03-13 12:32 | HBC-RTSCRFI-000026
CPMG-SUBRFI-000013: CPMG RFI 13- SAL and Security Management Plan
Responded | 2026-02-25 11:14 | We cannot access the SAL and Security Management plan on Aconex, can this be provided please. | PSA all information, the SAL will be included within the consultant appointment. If you have any issues please let us know | 2026-03-12 17:21 | HBC-RTSCRFI-000021
CPMG-SUBRFI-000014: CPMG RFI 14- Project Directory
Responded | 2026-02-25 14:54 | Can you please provide a Project Directory for the job. | Please see attached which is in doc register | 2026-03-02 10:14 | HBC-RTSCRFI-000005
CPMG-SUBRFI-000015: CPMG RFI 15- Existing Roof Build Up
Responded | 2026-02-26 11:24 | Please confirm existing roof build-up. | Please refer to existing Revit model recently provided and Stage 3 drawings | 2026-03-12 14:28 | HBC-GC-000029
CPMG-SUBRFI-000016: CPMG RFI 16- Openings at roof plant deck level on SE & MEP models
Responded | 2026-02-26 15:44 | Structural & MEP Models show what seem to be openings at roof plant deck level, see attachments “CPMG RFI 16 attachment 1”, “CPMG RFI 16 Attachment 2” & “CPMG RFI 16 attachment 3” Please clarify if these are proposed openings | If the openings show trimming steel and services passing through they are required | 2026-03-12 14:27 | HBC-GC-000031
CPMG-SUBRFI-000017: CPMG RFI 17- Concrete Bunker
Responded | 2026-03-17 17:51 | HB previously issued a pdf of the concrete bunker As you are aware there is a discrepancy of 25mm with current model. Can we please request the revit model to ensure the correct parameters are plotted on our model to include door and door cover and x ray equipment. | Please see attached | 2026-03-19 16:12 | CPMG-GC-000002
CPMG-SUBRFI-000018: CPMG RFI 18- Existing Steelwork
Responded | 2026-03-17 17:53 | Existing steelwork to grid appears to be missing on structural model but indicated on the pdfs- ca this be provided please for the revit model. | The grid will be on the Revit model attached to the response to RFI CPMG RFI 17- Concrete Bunker | 2026-03-19 12:21 | FDG-GC-000006
CPMG-SUBRFI-000019: CPMG RFI 19- AS02 Setting Out
Responded | 2026-03-18 09:35 | Updated design drawings on AS02 were received on 11.03.26 in PDF. It was highlighted the revised model will not be completed during Stage 4. It was requested the setting out of existing Stage 3 model be updated to suit the PDF. Existing set out of AS 02 1634mm from GL E. 5050mm from existing column flange GL14. Revised PDF drawing CD57776 General Arrangement set out of AS 02 1720mm from GL E and 4792mm from existing column flange GL14. Please confirm if existing Stage 3 model of AS 02 is to be set out to revised information. Please see attached. | Please see attached screenshot for setting out | 2026-03-19 12:01 | CPMG-GC-000004
CPMG-SUBRFI-000020: CPMG RFI 20- Plant Deck Stairs/Ramp
Responded | 2026-03-20 14:19 | The plant deck Stage 3 drawings adjacent to indicate steps GL 17 and GLB to C indicates steps whereas the model provided indicated ramps. Please confirm which one to proceed with. | The ramp is shown on the existing Building 200 model and never constructed. Please proceed with the stairs shown on the current information issued. Moving forward, please utilised the issued drawings for reference as these will reflect the current design information. | 2026-03-23 15:41 | HBC-RTSCRFI-000040
EDGEPS-CL-RFI-000009: AS02 / RM008A plant deck equipment
Overdue | 2026-03-17 13:37 | WP1 construction team to respond that this plant deck GA attached for AS02 in RM008A is acceptable and accounted for. | (blank) | (blank) | HBC-RFI-000075
Elect-SUBRFI-000001: Architects Model or DWGs
Closed-Out | 2026-01-27 11:29 | Please issue the latest Architects Model or DWG’s. | This has now been issued as part of Stage 3 pack. | 2026-02-19 12:47 | HBC-RTSCRFI-000001
Elect-SUBRFI-000002: Waterman Model or DWGs
Closed-Out | 2026-01-27 11:32 | Please issue the latest Waterman Model or DWG’s. | This has now been issued as part of Stage 3 pack. | 2026-02-19 12:48 | HBC-RTSCRFI-000002
Elect-SUBRFI-000003: 3-compartment trunking
Closed-Out | 2026-01-27 11:59 | Drawing MTCC-WBS-ZZ-GD-DR-ME-50208 - Proposed Enabling Works High Level Sheet 1 of 2_P02. Confirm the route of the 3-compartment trunking. Should this be installed between existing external wall and new inner wall? | Trunking for the services that sit behind the secure line must been run between the Remtech panel and the existing wall. these must not be brought back inside the secure line. | 2026-03-17 13:50 | HBC-RTSCRFI-000034
Elect-SUBRFI-000004: 3-compartment trunking along gridline 20
Closed-Out | 2026-01-27 12:00 | Drawing MTCC-WBS-ZZ-GD-DR-ME-50208 - Proposed Enabling Works High Level Sheet 1 of 2_P02. Can the new 3-compartment trunking along gridline 20 be installed between 2.5 & 3.0 metres affl for future access. If the trunking is routed between walls, does it need to be accessible in the future or will it be inaccessible when the inner wall is constructed. The depth of void needs increasing to allow persons to access with steps if future access is required. | (blank) | (blank) | HBC-GC-000034
Elect-SUBRFI-000005: Fire detection requirements within the new inner wall
Closed-Out | 2026-01-27 12:02 | Drawing MTCC-WBS-ZZ-GD-DR-ME-50208 - Proposed Enabling Works High Level Sheet 1 of 2_P02. Is fire detection required within the new inner wall being created? | (blank) | (blank) | EDGEPS-CL-RFI-000004
Elect-SUBRFI-000006: Electrical Isolations MTC process and permit system
Closed-Out | 2026-01-27 12:03 | Please provide confirm MTC process for Electrical Isolations. Do they have a permit system for us to follow? | (blank) | (blank) | HBC-GC-000040
Elect-SUBRFI-000007: Siemens Fire & Security mobilisation period
Closed-Out | 2026-01-27 12:04 | Siemens Fire & Security require 3 to 4 weeks to mobilize from placement of an order. This needs factoring in when programming works. No order has been placed yet. | (blank) | (blank) | HBC-GC-000041
Elect-SUBRFI-000008: Electrical Condition Report
Overdue | 2026-01-27 12:05 | Can we have copies of the latest Electrical Condition Report for the area for reference purposes. | (blank) | (blank) | WAT.-GC-000001
Elect-SUBRFI-000009: Existing As-installed drawings
Overdue | 2026-01-27 12:05 | Can we have copies of any previous as installed drawings for reference purposes. | Can we have an update on the requested please | 2026-03-17 07:52 | HBC-RTSCRFI-000033
Elect-SUBRFI-000010: Waterman P02 as construction drawings
Responded | 2026-01-27 12:06 | Confirm we are to work with Waterman P02 drawings for construction purposes. | (blank) | (blank) | HBC-GC-000042
Elect-SUBRFI-000011: New walls as enabling works
Closed-Out | 2026-01-27 12:07 | Will the new walls be installed as part of the enabling works? We need to understand what we are fixing the perimeter items too and at what stage. | Yes | 2026-03-11 15:35 | HBC-RTSCRFI-000007
Elect-SUBRFI-000012: Incumbent specialist dealing with the existing Siemens Lighting Controls
Closed-Out | 2026-02-19 13:25 | Can you please provide details on the Incumbent specialist dealing with the existing Siemens Lighting Controls. This will allow us to decommission the existing lighting. | Contact details for Siemens Aaron Chilver Siemens plc RC-GB SI RSS-EMEA NB Mobile: +44 7921245829 mailto:aaron.chilver@siemens.com | 2026-02-25 09:13 | HBC-GC-000045
Elect-SUBRFI-000013: Enabling - Removal of Lighting System Impacts adjacent Cell
Overdue | 2026-03-18 08:22 | Enabling - Removal of Lighting System Impacts adjacent Cell | (blank) | (blank) | HBC-GC-000048
Elect-SUBRFI-000014: Enabling - New Route of Containment Required into Plantroom
Overdue | 2026-03-18 08:27 | Enabling - New Route of Containment Required into Plantroom | (blank) | (blank) | HBC-GC-000047
Elect-SUBRFI-000015: (Watermans) Strip Out/Enabling Drawings
Outstanding | 2026-03-26 15:30 | (Watermans) Strip Out/Enabling Drawings in Revit/dwg format | (blank) | (blank) | HBC-RFI-000110
HBC-RFI-000001: Weight of Equipment / Machinery on New Raft Slab
Closed-Out | 2026-02-02 08:33 | Please could you provide the weight of the equipment/machinery that will be sitting on the new raft slab? | See below loading. The setting out can be found on within the architectural pack. | 2026-02-25 09:07 | WAT-RTRFI-000002
HBC-RFI-000002: Buidling Control Stage 3 Plan assessment
Overdue | 2026-02-13 15:10 | Budiling Control stage 3 Plan Assessement | Please see attached response from Warwick DC regarding the building regs application. Please note the inspection requirements in the letter to be picked up by HB. | 2026-03-27 13:48 | HBC-RTSCRFI-000042
HBC-RFI-000009: Design assumptions clarifications
Closed-Out | 2026-02-19 16:44 | Design assumptions clarifications | MTC Initial MEP Design Review - response | 2026-02-26 09:39 | EDGEPS-RTRFI-000003
HBC-RFI-000010: Clarifcations on Enabling works
Overdue | 2026-02-20 09:57 | Clarifcations on Enabling works | (blank) | (blank) | WAT.-GC-000006
HBC-RFI-000011: Pile cap size and setting out
Responded | 2026-02-24 14:40 | Pile cap size and setting out | See below response | 2026-02-24 15:23 | WAT-RTRFI-000001
HBC-RFI-000012: Mezz support steels
Responded | 2026-02-26 07:57 | Utilizing security panel support steels for Mezz support | see response below. | 2026-02-26 10:41 | WAT-RTRFI-000006
HBC-RFI-000013: Replace concrete decking for 38mm decking
Responded | 2026-02-26 08:03 | Replace concrete decking for 38mm decking | Please utilise concrete and not the 38mm decking | 2026-02-26 11:51 | FDG-RTRFI-000001
HBC-RFI-000014: Lidded areas
Responded | 2026-02-26 08:06 | Lidded areas | Lidded areas to be as drawn on the Fairhurst drawings | 2026-03-23 16:48 | HBC-RTSCRFI-000041
HBC-RFI-000015: Fire alarm - Aspirating Pipework
Responded | 2026-02-26 08:42 | • Aspirating pipework design – has this be designed by a specialist? • Details of retained Aspirating pipework need to be provided / detailed? | WBS - RIBA Stage 3 indication of design intent by WBS in house with input from Siemens (Aaron Chivers) who is familiar with the installation. Design based upon the installation of new pipework throughout. Should Contractor chose to retain any of the existing then validation report required for review by the MTC | 2026-02-26 08:43 | WAT.-RTRFI-000001
HBC-RFI-000016: Security Zones drawings
Responded | 2026-02-26 08:45 | • Security zones drawing has not been provided; please provide this information? | This has now been provided by Edge 24.02.2026 and issued out 25.02.2026 | 2026-02-26 08:48 | HBC-RTRFI-000001
HBC-RFI-000017: Electrical AFDDs
Responded | 2026-02-26 08:48 | •AFDD noted in specification are these required? | WBS - For this building type AFDD is a recommendation only for single phase outlets not exceeding 32A. To be discussed with the MTC, the opinion of WBS is that this is not required for this building. | 2026-02-26 08:50 | WAT.-RTRFI-000003
HBC-RFI-000018: Atex Zones
Overdue | 2026-02-26 08:51 | •Atex zones need to show on the drawings and coordinated on an electrical drawing – can this be provided please. | WBS - To be addressed as part of RIBA Stage 4 with MTC. This action is currently with the MTC/client to advise | 2026-02-26 08:53 | HBC-GC-000051
HBC-RFI-000019: Emergency Lighting & high risk lighting
Responded | 2026-02-26 08:55 | • High-risk emergency lighting needs to be detailed this is not currently shown – please provided areas requiring High risk lighting? • High bay emergency lighting has been removed, and integral 3hr liner fittings have been shown, this appears the incorrect method for this large area and if high-risk lighting is required. • Emergency lighting – Please confirm test method? 3 methods shown. | WBS - High risk lighting areas are deemed to be the main workshop area. RIBA Stage 3 indication of design intent. Final design of luminaires and final selection to be agreed with MTC/Fire Officer as part of RIBA Stage 4 design works. Emergency lighting testing method to be selected to suit the solution for how the emergency lighting to be provided. | 2026-02-26 08:56 | WAT.-RTRFI-000005
HBC-RFI-000020: MEP Specification items not needed
Closed-Out | 2026-02-26 08:57 | Items still left in specification despite noted as not required on tracker, assume not needed: Sprinker and Fire alarm items. Pagers , Vibrating Pillows. | WBS - Confirmed not required. | 2026-02-26 08:58 | WAT.-RTRFI-000006
HBC-RFI-000021: UPS
Closed-Out | 2026-02-26 08:59 | • UPS supplies noted in standard cables, Tracker states to be fire rated now, Updated LV schematic show non fire rated, assume these are to be fire rated now? assume fire survival time taken also in to account and these have been increased by two conductor sizes as stipulated in the BS. | WBS - Cables for UPS supplies to be fire rated. | 2026-02-26 09:00 | WAT.-RTRFI-000007
HBC-RFI-000022: Generator quantity and requirements
Responded | 2026-02-26 09:02 | • Generator fuel polishing noted now in Tender query return but not in the updated specification – assumed required? Two Generators shown on drawing, assume only one required ? | WBS - Fuel polishing required for generator fuel 1No. 1500kVA generator set only required. | 2026-02-26 09:03 | WAT.-RTRFI-000008
HBC-RFI-000023: Fire Strategy
Responded | 2026-02-26 09:10 | • Please provide fire strategy. | Fire Strategy will form part of the HAZZOP which is being developed by MTC representative. Fire Alarm Specialist contractor to develop strategy as part of RIBA Stage 4. | 2026-02-26 09:11 | EDGEPS-RTRFI-000002
HBC-RFI-000024: Space Heating Demands
Responded | 2026-02-26 09:14 | • Stage 3 design only accounts for the heating of the air volumes and not space heating demands. | Fabric and infiltration heat losses haven't been calculated for this RIBA3 issue but there is an intention to take this into account during RIBA4. | 2026-02-26 09:15 | WAT.-RTRFI-000009
HBC-RFI-000025: Cooling Load Assessment
Responded | 2026-02-26 09:17 | • No cooling load assessment has been carried out at stage 3. | Refer to Alpha RFI ref 40. Cooling load for equipment and associated operating diversity is still subject to RFI. The use of the existing AHUs provides a maximum cooling capacity based on a given maximum flow rate and an optimally maximum supply to room delta t. MTC will need to advise whether this is sufficient for the expected individual equipment loads / operating diversity. Solar and transmittance loads have not been taken account of but are expected to be minimal due to the total lack of glazing. | 2026-02-26 09:20 | WAT.-RTRFI-000010
HBC-RFI-000026: Ventilation - Alpha reports
Responded | 2026-02-26 09:48 | • Alpha Technical Report states “potential cooling coil (served by the new ASHP)” and that it may be necessary to provide cooling coils to the existing supply AHUs via new frost coils & ASHP. • Alpha Technical Report only states “supplementary heating and cooling of the C0 areas is proposed with new in room AC units as required” - No concept sizes provided • Alpha Report states X-ray cooling system may be excessive and impact HVAC design – Please provide details. | There is space in the existing AHUs to accommodate cooling coils. The existing frost coils are LPHW. There has been no design development carried out for supplementary cooling / heating of the C0 areas. The RIBA3 G.A.s show the use of air to air reversible heat pumps. This has subsequently been deemed inappropriate due to the need for third parties to access the secure facility to carry out maintenance activities. The expectation is that the RIBA4 design will change this arrangement to include zoned air supply with cooling / re-heat coils located outside of the secure area. The cooling load for the X-ray equipment has not yet been identified but is expected to be captured during RIBA4. | 2026-02-26 10:08 | WAT.-RTRFI-000011
HBC-RFI-000027: Refrigerant requiremenets
Responded | 2026-02-26 10:11 | No refrigerant specified – Is leak detection, alarms, automatic isolation required? | WBS have included provision for the O₂ depletion detection system within the secure facility, as shown on the layouts, mainly shown on 200SF4-WBS-01-GF-DR-M-54201 (P06) and detailed in the specification. The system provides the monitoring and alarm strategy associated with oxygen displacement risks within SF4, noting the gas detection panel located in the entrance lobby and sounder / beacons located within the SF4 facilities. Following this HAZOP, particularly under fault, purge, emergency shutdown or loss of power scenarios has not yet been confirmed by the client team. Any additional design measures / changes to the emergency Argon strategy or enhanced local alarms, can be incorporated into the RIBA Stage 4 contractor design package. At this stage, therefore, the design intent is: • Stage 3 (WBS): O₂ depletion system included and shown on layouts. • Stage 4 (Contractor): To be defined and incorporated if identified by the HAZOP | 2026-03-17 14:14 | HBC-RTSCRFI-000037
HBC-RFI-000028: Plant Deck Coordination and Combined Services
Closed-Out | 2026-02-26 10:12 | Has plant deck special co-ordination accounting for all equipment and specialist design been carried out? Please provide Combines Services Roof Plant Deck Layouts. | Yes - Coordinated plan drawings to be issued by WBS on Monday 23rd c/w Issue sheet. | 2026-02-26 10:14 | WAT.-RTRFI-000012
HBC-RFI-000029: Drainage Layouts TBC equipment
Responded | 2026-02-26 10:21 | Drainage Layouts state some areas/equipment still TBC (I.e. AS01) – Please provide information. | WBS - To be develop by HB - Note should reference AS02 as drainage tanks beneath platform. Closed | 2026-02-26 10:22 | WAT-RTRFI-000003
HBC-RFI-000030: Water services - schedule TBC items
Responded | 2026-02-26 10:31 | Water Services - Water Schematics provided – Process Water Schedule identifies many items still TBC – Please provide information. | WBS - Process Tanks and primary pumps sizes as detailed on layout / schedules. HB to take forward and confirm as part of RIBA Stage 4 design works | 2026-02-26 10:32 | WAT.-RTRFI-000013
HBC-RFI-000031: Water Services - Specification risk
Responded | 2026-02-26 10:39 | Specification states “Final tank capacity, booster-set duty requirements, operational sequencing, resilience philosophy, and all associated safety considerations shall be developed and confirmed by the Contractor as part of the detailed design and shall be subject to HAZOP review and approval” Risk to Program / Cost | RIBA Stage 3 satisfies design intent. Process Tanks and primary pumps sizes detailed on layout / schedules. Operating pressures/flows to be coordinated in Stage 4 once EM data is provided. | 2026-02-26 10:45 | WAT.-RTRFI-000014
HBC-RFI-000032: Compressed Air - schematics
Responded | 2026-02-26 10:48 | Compressed Air Schematic/specification – Pressures and flow rates still TBC in many instances – Please provide information | TBC items depend on final machine data. Stage 3 satisfies design intent; final operating pressures/flows to be coordinated in Stage 4 once EM data is provided | 2026-02-26 10:49 | WAT.-RTRFI-000015
HBC-RFI-000033: Compressed Air - Specification
Responded | 2026-02-26 10:50 | Specification states “Operational requirements, duty cycle and usage profile of the compressed air system remain unknown at this stage. The Final operation and control strategy shall be confirmed and fully reviewed at the next design stage once end-user input and equipment specific data becomes available” Risk to programme / cost. Please provide updated information. | TBC items depend on final machine data. Stage 3 satisfies design intent; final operating pressures/flows to be coordinated in Stage 4 once EM data is provided | 2026-02-26 10:51 | WAT.-RTRFI-000016
HBC-RFI-000034: Specification - Emergency Lighting
Responded | 2026-02-26 10:53 | Emergency Lighting spec is all over the place - manual key switch, self test, monitored, central battery etc. | WBS - The stage 3 specification offers opportunity for design development during Stage 4. Taking into account minimising routine maintenance into the secure areas. | 2026-02-26 10:54 | WAT.-RTRFI-000017
HBC-RFI-000035: Specification - LV Cable Sizes
Responded | 2026-02-26 14:35 | Cable sizes for main LV cables are massively undersized | WBS - RIBA Stage 3 indication of design intent. Final selection of all cabling including sizes to be developed as part of RIBA Stage 4 design for review. | 2026-02-26 14:35 | WAT.-RTRFI-000018
HBC-RFI-000036: Specification - Main incomers
Responded | 2026-02-26 14:37 | Main Incomers on Main Switchboard are incorrect and rated at 4000A. HV Transformers are shown as 3000kVA but a side note says this is to be 1500kVA. | WBS - RIBA Stage 3 depicts incorrectly sized protective device. Stage 3 design based upon 2No. 1.5MVA transformers. Stage 4 design to validate the load assessment and develop as part of their Stage 4 design. | 2026-02-26 14:37 | WAT.-RTRFI-000019
HBC-RFI-000037: Specification - ladder rack
Responded | 2026-02-26 14:43 | Ladder rack still identified going up the external side of the building. | WBS - Revision P07 of the layout indicates the ladder containment to be internal and should be the basis for the Stage 4 design. | 2026-02-26 14:44 | WAT.-RTRFI-000020
HBC-RFI-000038: Specification - Tempest filters
Responded | 2026-02-26 14:56 | Tempest filters shown at 1200A but fuse protection from main panel are shown as 1250A. This is conflicted and we would need to increase the filter to the 1600A version. For example, the 1200A version is £40k and the 1600A version is £110k. | WBS - Stage 4 Designers to verify and validate loadings and develop as part of their Stage 4 design. Please also note 1200A rated fuse is available to match the sizes of the Power filters shown. | 2026-02-26 14:56 | WAT.-RTRFI-000021
HBC-RFI-000039: Specification - Submains / DBs / UPS / Illuminance
Responded | 2026-02-26 14:59 | 1. Spec says essential submains should be FP600, no FP600 submains shown on schematics - only SWA. 2. Spec mentions both 20% and 25% spare on distribution boards. Which is true? 3. Clarification on UPS size required 175kW N+1 or 200kW N? Former has much more resilience, latter is more cost effective and still provides resilience, albeit limited. 4. Illuminance uniformity levels contradict each other in spec, 0.4/0.6 in table and 0.8 in body of text. | 1. WBS - No essential supplies, generator backed provision only for safe shutdown 2. WBS - Stage 4 design to provide Distribution Boards with 25% spare capacity. 3. WBS - 175kW N+1 to be provided. 4. WBS - values of 0.4/0.6 in table to be used. | 2026-02-26 15:00 | WAT.-RTRFI-000022
HBC-RFI-000040: Specification Secure walls - Penetrations / fixings
Responded | 2026-02-26 15:17 | 1. MTC standard details for penetrations through walls? 2. Details of secure wall build ups for fixings / penetrations etc. | 1. Standard penetration details are included at Stage 3 Package; Contractor must adapt these for final construction as part of Stage 4 design. Taking into account the security accreditation required to meet NPSA accreditation. 2. Standard details are provided by the wall panelling manufacturer to ensure compliance to NPSA requirements. Typical details on structural detail drawings. | 2026-02-26 15:19 | WAT.-RTRFI-000023
HBC-RFI-000041: Specification - Generator
Responded | 2026-02-26 15:43 | Generator runtime / autonomy? | WBS - RIBA Stage 3 stipulates 12 hours +10%. Final generator runtime requirements to be confirmed with MTC. | 2026-02-26 15:46 | WAT.-RTRFI-000024
HBC-RFI-000042: Specifications - PIRs or Microwave detectors
Responded | 2026-02-26 15:48 | Microwave detectors are shown on lighting drawings, PIR's in spec? PIR's would be more appropriate. | WBS - RIBA Stage 3 indication of design intent. Final selection of detectors to be developed as part of RIBA Stage 4 design in conjunction with MTC. Note the selection of any devices needs to meet with the requirements of STAMP accreditation. | 2026-02-26 15:49 | WAT.-RTRFI-000025
HBC-RFI-000043: Specification - Water requirements
Responded | 2026-02-26 15:52 | The daily operation & quantity of water has not been determined by the client team. Can this be qualified? | RIBA Stage 3 satisfies design intent. Process Tanks and primary pumps sizes detailed on layout / schedules. Operating pressures/flows to be coordinated in Stage 4 once EM data is provided. | 2026-02-26 15:53 | WAT.-RTRFI-000026
HBC-RFI-000044: Specification - LEV System drainage
Responded | 2026-02-26 16:23 | Drainage type for the Lev System to be used is referenced as being TBC in Waterman Stage 3 Specification, can this be confirmed? | Please Clarify ? Drainage type for LEV equipment will be confirmed following final equipment specifications at Stage 4. | 2026-02-26 16:24 | WAT.-RTRFI-000027
HBC-RFI-000045: Specification - Existing AHU Control Panels
Responded | 2026-02-26 16:25 | The existing controls panel can be reused (if viable) to form the new AHU control panels, as instructed by Waterman Stage 3 Specification. Can details of the existing panels be provided? | Could you also please confirm whether Henry Brothers has engaged with the incumbent BMS contractor, Electrack (Phil Randle), for input? His understanding of the existing control architecture and integration requirements will be valuable in assessing any dependencies or constraints on the proposed modifications. | 2026-03-17 12:30 | HBC-GC-000044
HBC-RFI-000046: Specification - MTC Regulatory Facility Consideration Report
Responded | 2026-02-26 16:29 | Reference is made in Waterman Stage 3 Specification to 'MTC Regulatory Facility Consideration Report'. Can this document be provided? | This reference is not a required deliverable and can be ignored. | 2026-03-17 17:06 | HBC-GC-000046
HBC-RFI-000047: Specification - Acoustic Report
Overdue | 2026-02-26 16:36 | Is an acoustic report for the project available for use? This will be essential for plant selections. | (blank) | (blank) | HBC-RFI-000047
HBC-RFI-000048: Ventilation - Alpha Engineering RFIs
Closed-Out | 2026-02-26 16:38 | Attached set of Alpha Engineering RFIs were included within the Stage 3 pack which are still listed outstanding. Can their status be clarified | These were RFIs raised by Alpha Engineering with the expectation that any resolution would be carried into RIBA4. | 2026-02-26 16:43 | HBC-GC-000054
HBC-RFI-000049: Compressed Air - end user flow rates, pressures & air quality
Responded | 2026-02-26 16:44 | Clarification required of flow rates, pressures & air quality of all proposed end user equipment. A number of TBCs are noted on the Waterman schematic dwg. | CA allowances have been made on main plant, refer to quotation as detailed within specification on flow rate, pressure and air quality. Stage 4 Contractor must obtain final data and coordinate drops, pressures & filtration classes. | 2026-02-26 16:49 | WAT.-RTRFI-000029
HBC-RFI-000050: Compressed Air - Pipework alternative
Closed-Out | 2026-02-26 16:50 | Pipework specified as TESEO, we understand this is no longer available in the UK & would therefore propose that an aluminium alternative such as Trans Air or similar be used. | Alternatives may be proposed via formal Technical Submission during Stage 4, subject to equal‑or‑approved compliance. | 2026-02-26 16:50 | HBC-GC-000022
HBC-RFI-000051: Argon - flow rate & frequency of tank replenishment
Responded | 2026-02-26 16:54 | Clarification required for Argon flow rate & frequency of tank replenishment. This will inform the finalised design. | Confirmed as TBC pending EM operational cycles. Final values will be validated during Stage 4 HAZOP and EM engagement | 2026-02-26 16:55 | WAT.-RTRFI-000031
HBC-RFI-000052: Argon - Flow Meter
Responded | 2026-02-26 16:56 | Is there a specification of flow meter required, currently not detailed in Stage 3 proposal. | Refer to Mechanical Specification. 6.6.3 and page 67. Both Emergency and high pressure argon system metered. To be determine as part of RIBA Stage 4 works. | 2026-02-26 16:58 | WBS Ltd-GC-000002
HBC-RFI-000053: Argon - pressure for AS3/4
Responded | 2026-02-26 17:00 | Confirmation required of the pressure for AS3/4 (RM034 Swarf Management), shown as TBC. | Design intent provided. Final pressure requirements for AS03/AS04 will be determined following EM confirmation. | 2026-02-26 17:01 | WAT.-RTRFI-000033
HBC-RFI-000054: Argon - Specific pressure
Responded | 2026-02-26 17:03 | Clarity needed on reference to +16 Bar max. working pressure, can a specific pressure not be confirmed? | Argon system based on 16barg Working Pressure (15.5barg Nominal) to suit AS05. Stage 4 Contractor must obtain final equipment information to form part of RIBA Stage 4 design works. | 2026-02-26 17:03 | WAT.-RTRFI-000034
HBC-RFI-000055: Equipment Service Feeds - Clarification Matrix
Responded | 2026-02-27 13:01 | Please can the attached matrix be filled in by MTC / Waterman clarifying flow rates / pressures etc. | The clarification matrix provided appears to simply replicate the WBS Stage 3 placeholder values. In line with the SF4 Mechanical Specification, all flow rates, pressures, service demands and equipment consumption values must be confirmed, validated and populated by the Contractor as part of their coordinated Stage 4 design development. HB is therefore required to populate the matrix based on: their coordinated Stage 4 mechanical and specialist gas design, confirmed equipment requirements from the end user, and all validation checks undertaken during their Stage 4 design process. Once HB have populated the clarification matrix with their verified design inputs, WBS/MTC will review and provide comment/acceptance as part of the Stage 4 design review process. | 2026-03-19 16:01 | EDGEPS-GC-000005
HBC-RFI-000058: Existing SVP and Gullies
Responded | 2026-03-02 13:49 | Existing SVP and Gullies | SF4 Works - Above Ground Drainage. The SVP located on Grid Line U20 is required to be extended to suit the proposed drainage arrangement. All internal drainage from the cell is directed to the IBC via a pumped solution in accordance with the Stage 3 drainage strategy. As the Stage 4 design development sits with the contractor, HB shall validate the Stage 3 assumptions and confirm whether the SVPs on both GL B20 and GL K20 remain necessary, or whether either can be removed or capped if not required as part of the final drainage and venting strategy. | 2026-03-17 14:05 | HBC-RTSCRFI-000036
HBC-RFI-000072: Height for new trunking under crane steel
Responded | 2026-03-12 15:28 | Height for new trunking running under the existing crane steel, This shows on the watermans drawings as a continuation of existing trunking. Please confirm this is acceptable. | Proposal to run new trunking as a continuation of the existing trunking, noted and accepted. | 2026-03-18 16:22 | WAT.-RTRFI-000042
HBC-RFI-000073: CCTV containment route
Responded | 2026-03-12 15:34 | Route of new containment for existing CCTV, Electract have proposed to conduit from existing locations to sf4 plant area data cabinets, This was suggested by JDC networks and Siemens who are MTC incumbents. Please confrim this is acceptable | MTC to advise if acceptable from a Security perspective. | 2026-03-13 16:07 | HBC-GC-000035
HBC-RFI-000074: Natural Gas
Responded | 2026-03-12 15:38 | Natural Gas, WB need to purge and remove the pipe work within SF4 and in the SF4 Plant Deck. Can WB purge and remove this pipework? WB will need support from facility’s in regards to Drawings for the feed of the Natural Gas, shutoff points, purge points and effects to other Cells. Works would like to commence WC23/03 please cofirm asa built infomation. | This query refer to ARC Clearance - Phase 2 Works Not SF4 works. As Defined in the strip out responsibilities, please note: The contractor is responsible for the full validation, purging, isolation and removal of all redundant Natural Gas pipework forming part of the Phase 2 works, to be carried out by a competent Gas Safe subcontractor. All existing gas installations must be site validated prior to commencement, including tracing of pipework, confirming isolation points and identifying any shared feeds to other cells. MTC will provide any available historic as installed information; however, this cannot replace the requirement for full contractor validation. No removal works may proceed until all isolations have been confirmed through the Permit to Work process. WBS has yet to receive HB's own Stage 4 strip-out drawings and set of RAMS for approval by the MTC representatives prior to commencing the strip-out works. | 2026-03-17 13:52 | HBC-GC-000043
HBC-RFI-000080: Alpha - Breakout area containment arrangements 2529-RFI-PROJ-001
Outstanding | 2026-03-20 13:08 | Alpha - Breakout area containment arrangements 2529-RFI-PROJ-001 | (blank) | (blank) | EDGEPS-GC-000006
HBC-RFI-000081: Alpha - Heat emission from equipment 2529-RFI-PROJ-002
Outstanding | 2026-03-20 13:13 | Alpha - Heat emission from equipment 2529-RFI-PROJ-002 | (blank) | (blank) | EDGEPS-GC-000007
HBC-RFI-000082: Alpha - Filter mist data 2529-RFI-PROJ-003
Outstanding | 2026-03-20 13:15 | Alpha - Filter mist data 2529-RFI-PROJ-003 | (blank) | (blank) | EDGEPS-GC-000008
HBC-RFI-000083: Alpha - VIM furnace vacuum pump data 529-RFI-PROJ-004
Outstanding | 2026-03-20 13:17 | Alpha - VIM furnace vacuum pump data 529-RFI-PROJ-004 | (blank) | (blank) | HBC-RFI-000083
HBC-RFI-000084: Alhpa - VIM furnace vacuum pump operation2529-RFI-PROJ-005
Outstanding | 2026-03-20 13:19 | Alhpa - VIM furnace vacuum pump operation2529-RFI-PROJ-005 | (blank) | (blank) | HBC-RFI-000084
HBC-RFI-000085: Alpha - Heat treatment equipment filtration2529-RFI-PROJ-006
Outstanding | 2026-03-20 13:22 | Alpha - Heat treatment equipment filtration2529-RFI-PROJ-006 | (blank) | (blank) | HBC-RFI-000085
HBC-RFI-000086: Alpha - X-ray ozone generation 2529-RFI-PROJ-007
Outstanding | 2026-03-20 13:26 | Alpha - X-ray ozone generation 2529-RFI-PROJ-007 | (blank) | (blank) | HBC-RFI-000086
HBC-RFI-000087: Alpha - Carbon analyser LEV requirement 2529-RFI-PROJ-008
Outstanding | 2026-03-20 13:29 | Alpha - Carbon analyser LEV requirement 2529-RFI-PROJ-008 | (blank) | (blank) | HBC-RFI-000087
HBC-RFI-000088: Alpha - Expectations for ventilation system operation under fire philosophy 2529-RFI-PROJ-009
Outstanding | 2026-03-20 13:32 | Alpha - Expectations for ventilation system operation under fire philosophy 2529-RFI-PROJ-009 | (blank) | (blank) | HBC-RFI-000088
HBC-RFI-000090: Alpha - Control System Details2612-RFI-PROJ-010
Responded | 2026-03-20 15:21 | Alpha - Control System Details2612-RFI-PROJ-010 | see message below | 2026-03-20 15:30 | Quantem-RTRFI-000001
HBC-RFI-000092: Alpha - EC&I Client Side Contacts Request2612-RFI-PROJ-012
Outstanding | 2026-03-20 15:28 | Alpha - EC&I Client Side Contacts Request2612-RFI-PROJ-012 | (blank) | (blank) | HBC-RFI-000092
HBC-RFI-000093: Alpha - Existing AHU Information – Including Fan Data 2612-RFI-PROJ-013
Outstanding | 2026-03-20 15:30 | Alpha - Existing AHU Information – Including Fan Data 2612-RFI-PROJ-013 | (blank) | (blank) | HBC-RFI-000093
HBC-RFI-000095: Alpha - Cable Type - Assumptions2612-RFI-PROJ-015
Outstanding | 2026-03-20 15:36 | Alpha - Cable Type - Assumptions2612-RFI-PROJ-015 | (blank) | (blank) | HBC-RFI-000095
HBC-RFI-000096: Alpha - MTC Tagging Standard – HVAC2612-RFI-PROJ-016
Outstanding | 2026-03-20 15:41 | Alpha - MTC Tagging Standard – HVAC2612-RFI-PROJ-016 | (blank) | (blank) | HBC-RFI-000096
HBC-RFI-000097: Alpha - MTC Tagging Standard – EC&I 2612-RFI-PROJ-017
Outstanding | 2026-03-20 15:44 | Alpha - MTC Tagging Standard – EC&I 2612-RFI-PROJ-017 | (blank) | (blank) | HBC-RFI-000097
HBC-RFI-000098: Alpha - Vendor List – Framework / Approved Suppliers 2612-RFI-PROJ-018
Outstanding | 2026-03-20 15:47 | Alpha - Vendor List – Framework / Approved Suppliers 2612-RFI-PROJ-018 | (blank) | (blank) | HBC-RFI-000098
HBC-RFI-000099: Alpha - Control Philosophy / BCD Provision2612-RFI-PROJ-019
Outstanding | 2026-03-20 15:55 | Alpha - Control Philosophy / BCD Provision2612-RFI-PROJ-019 | (blank) | (blank) | HBC-RFI-000099
HBC-RFI-000102: Composite deck quires - floor deck
Outstanding | 2026-03-23 10:09 | Composite deck quires - floor deck | (blank) | (blank) | HBC-GC-000056
HBC-RFI-000103: Composite deck - Reinforcement quires
Outstanding | 2026-03-23 10:11 | Composite deck - Reinforcement quires | (blank) | (blank) | HBC-RFI-000103
HBC-RFI-000104: Composite deck - detialing quires
Outstanding | 2026-03-23 10:12 | Composite deck - detialing quires | (blank) | (blank) | HBC-RFI-000104
HBC-RFI-000105: VIM furnace floor loadings
Outstanding | 2026-03-23 16:57 | VIM furnace floor loadings | (blank) | (blank) | HBC-RFI-000105
HBC-RFI-000106: Alpha Engineering - PI Level
Outstanding | 2026-03-24 15:43 | Alpha Engineering - PI Level | (blank) | (blank) | HBC-RFI-000106
HBC-RFI-000108: Mezzanine deck design loads
Outstanding | 2026-03-25 09:08 | Mezzanine deck design loads | (blank) | (blank) | HBC-RFI-000108
WBL 1919-SUBRFI-000001: Compressed Air Diversity of Use
Outstanding | 2026-03-27 11:04 | Can it be confirmed if there is a known level of 'diversity of usage' factor (can be expressed as a percentile) that can be applied to the compressed air system? This will inform the physical sizing of the system & ensure that it is best sized to suit the facility's true/actual anticipated operation & usage patterns | (blank) | (blank) | WBL 1919-SUBRFI-000001

## ProjectInfo (hidden)
Project Name | Date Generated
MTP | 2026-03-27 14:36